## Sheet1
Model Name | CPS SCA50KTL-DO/EU-400
DC Input
Rated DC Input Power | 51.5KW
Max. DC Input Power / each MTTP | 67.5KW / 22.5KW
Max. DC Input Voltage | 1100VDc
Operating DC Input Voltage Range | 200 - 1000Vdc
MPPT Voltage range (Full Load) | 540 -850Vdc
Start-up DC Input Voltage / power | 330V / 80W
Rated DC Input Voltage | 635V
Number of MPPT / Number of DC Input | 3 / 3+3+3
Max.Input Current | 3 *32A
DC Disconnection Type | Integrated DC Switch
AC Output
Rated AC Output Power | 50KW
Max. AC Output Power | 55KVA
Rated Output Voltage | 230 / 400Vac
Output Voltage Range* | 320 - 460Vac
Grid Connection Type | 3(fay)/N(Option) / PE
Max AC Output Current | 80A
Rated Output Frequency | 50Hz/60Hz
Output Frequency Range* | 45Hz-55Hz / 55Hz-65Hz
Power Factor | >0.99(+-0.8 adjustable)
Current THD | <3%
AC Discounnection Type | _
System Data
topology | Transformerless
Max. Efficiency | 98.5%
Euro Efficiency | 98.4%
Stand-by / Night Consumption | <20W / < 1W
Environment Data
Protection Degree | IP65
Cooling | Variable speed cooling fans
Operating Temperature Range | -25C - +60C (derating from +45C)
Operating Humidity | 0 - 100%, Non-condensing
Operating Altitude | 4000m (derating from 3000m)
Display and Communication
Display | LCD + LED
Communication | Standard: RS485 / Option:PLC & Ethernet
Mechanical Data
Dimensions (W*H*D)[mm] | 600 * 826 * 260
Weight[Kg] | 65
Safety
Safety and EMC Standard | LVD:2006/95/EC EMC: 2004/108/EC,IEC/EN 62109-1:2010,IEC/EN62109-2:2011;IEC/EN61000-6-2:2005,1EC/EN61000-6-3:2007, NB/T 320004-2014;GT/T19964-2012
Grid Standard | IDC61727 / IEC62116