## Sheet1
Model Name | CPS SCA3KTL-SM | CPS SCA4KTL-SM | CPS SCA5KTL-SM | CPS SCA6KTL-SM
DC Input
Rated DC Power | 3350W | 4450W | 5550W | 6050W
Max. DC Voltage |  | 600Vdc
MPPT Voltage Range |  | 90 - 580Vdc
Rated DC Voltage |  | 360Vdc
Start Voltage |  | 90Vdc
Min. DC Voltage |  | 70Vdc
Max. DC Current PV1 / PV2 |  | 11A / 11A
Number of DC Connection Sets per MPPT |  | 1 / 1
Number of MPPT |  | 2
DC Switch |  | Optional
AC Output
Rated AC Power | 3000W | 4000W | 5000W | 6000W
Max. AC Power | 3300VA | 4400VA | 5500VA | 6000VA
Rated AC Current | 13.6A | 18.1A | 22.7A | 27.3A
Max. AC Current | 14.3A | 19.1A | 23.8A | 27.3A
Rated AC Voltage / Range |  | 220V, 230V, 240V / 180-280V
Grid Frequency / Range |  | 50+-5Hz
Power Factor(cos fay) |  | +-0.8(adjustable)
Current THD |  | < 3%
Grid Connection Type |  | L + N + PE
Efficiency
Max. Efficiency | 97.6% | 97.6% | 97.8% | 98%
Euro Efficiency | 97.2% | 97.3% | 97.3% | 97.4%
MPPT Efficiency |  | >99.5%
Protection
Internal Over-voltage Protection |  | Integrated
DC Insulation Monitoring |  | Integrated
DCI Monitoring |  | Integrated
GFCI Monitoring |  | Integrated
Grid Monitoring |  | Integrated
AC Short Circuit Current Protection |  | Integrated
Thermal Protection |  | Integrated
Anti-islanding Protection Monitoring |  | AFD
Interface
AC Connection |  | Plug-in Connector
DC Connection |  | MC4 / H4
LCD / LED Display |  | LED * 3+APP(Bluetooth)
Language |  | Chinese / English
Communication |  | RS232(Standard) / Wi-Fi & GPRS & RS485(Optional)
General Data
Topology |  | Transformerless
Consumption at Night |  | <0.2W
Consumption at Standby |  | 6W
Operating Temperature Range |  | -25C to +60C (45C to 60C with derating)
Cooling Method |  | Natural Convection
Ambient Humidity |  | 0 - 100%, Non-condensing
Altitude |  | 4000m (2000m with derating)
Noise |  | < 25dBA
Ingress Protection |  | IP65
Dimensions (W*H*D)[mm] |  | 335*426*125
Weight[kg] |  | 12.8
Warranty [Year] |  | 5 (Standard) / 10 / 15 / 20 / 25 (Optional)
Certification |  | IEC62109-1/2, IEC61000-6-1/2/3/4, IEC61727/62116, IEC61683