## Sheet1
INPUT DATA | SYMO 3.0-3-S | SYMO 3.7-3-S | SYMO 4.5-3-S | SYMO 3.0-3-M | SYMO 3.7-3-M | SYMO 4.5-3-M
Max. input current (I dc max 1/Idc max 2^1) |  |  | 16.0 A / 16.0 A
Max. array short circuit current (MPP1/MPP2) |  |  | 24.0 A / 24.0 A
Min. input voltage (Udc min) |  |  | 150 V
Feed in start voltage (Udc start) |  |  | 200 V
Nominal input voltage (Udc,x) |  |  | 595 V
Max. input voltage (Udc max) |  |  | 1000V
MPP voltage range (Umpp min -Umpp max) | 200 - 800 V | 250 - 800 V | 300 - 800 V |  | 150 - 800 V
Number MPP trackers |  | 1 |  |  | 2
Numbers of DC connection |  | 3 |  |  | 2+2
Max.PV generator output (Pdc max) | 6.0 KW (peak) | 7.4 KW (peak) | 9.0 KW (peak) | 6.0 KW (Peak) | 7.4 KW (peak) | 9.0 KW(peak)
OUTPUT DATA
AC nominal output (pax, x) | 3,000W | 3,700W | 4,500W | 3,000W | 3,700W | 4,500W
Max. output power | 3,000VA | 3,700VA | 4,500VA | 3,000VA | 3,700VA | 4,500VA
AC output current (Inc mm) | 4.3A | 5.3A | 6.5A | 4.3A | 5.3A | 6.5A
Grid connection (voltage range) |  | 3-NPE 400 V / 230 V OR 3-NPE 380 V / 220V (+20% / 30%)
Frequency (Frequency range) |  | 50 Hz / 60 Hz (45 -65 Hz)
Total harmonic distortion |  | < 3%
Power factor (cos fay ac,r) |  | 0.70 - 1 ind. / cap |  |  | 0.85 - 1 ind, / cap
GENERAL DATA
Dimensions (height x width x depth) |  |  | 645 x 431 x 204mm
Weight | 16.0kg |  |  |  | 19.9kg
Degree of protection |  |  | IP65
Protection class |  |  | 1
Overvoltage category (DC/AC)^2 |  |  | 2 / 3
Night time consumption |  |  | < 1 W
Inverter design |  |  | Transformerless
Cooling |  |  | Regulated air cooling
Installation |  |  | Indoor and Outdoor installation
Ambient temperature range |  |  | -25 … +60C
Permitted humidity |  |  | 0 ~ 100%
Max. altitude |  | 2,000 m / 3,400m (unrestricted / restricted voltage range)
DC connection technology | 3x DC+ and 3x DC-screw terminals 2.5 - 16 mm^2 |  |  | 4x DC+ and 4x DC-screw terminals 2.5 - 16 mm^2
AC Connection technology | 5 pole AC screw terminals 2.5 16 mm^2 |  |  | 5 pole AC screw terminals 2.5 16 mm^2
Certification and compliance with standards | OVE / ONORM E 8001.4 712, DIN V VDE 0126-1-1/A1, VDE AR N 4105,IEC 62109-1/2,IEC 62116,IEC 61727,AS 3100,AS 4777-2, AS 4777-3, CER 06-190,G83/2,UNE 206007-1,SI 4777, CEI0.21 ,NRS 097
EFFICIENCY
Max. efficiency |  |  | 98.0A
European efficiency (nEU) | 96.2% | 96.7% | 97% | 96.5% | 96.9% | 97.2%
n at 5 % pac.r^1 | 80.3 / 83.6 / 79.1 % | 83.4 / 86.4 / 80.6 % | 84.8 / 88.5 / 82.8 % | 79.8 / 85.1 / 80.8 % | 81.6 / 87.8 / 82.8 % | 83.4 / 90.3 / 85.0 %
n at 10 % pac.r^1 | 87.8 / 91.0 / 86.2 % | 90.1 / 92.5 / 88.7 % | 91.7 / 93.7 / 90.3 % | 86.5 / 91.6 / 87.7 % | 87.9 / 93.6 / 90.5 % | 89.2 / 94.1 / 91.2 %
n at 20 % pac.r^1 | 92.6 / 95.0 / 92.6 % | 93.7 / 95.7 / 93.6 % | 94.6 / 96.3 / 94.5 % | 90.8 / 95.3 / 93.0 % | 91.9 / 96.0 / 94.1 % | 92.8 / 96.5 / 95.1 %
n at 25 % pac.r^1 | 93.4 / 95.6 / 93.8 % | 94.5 / 96.4 /94.7 % | 95.2 / 96.8 / 95.4 % | 91.9 / 96.0 / 94.2 % | 92.9 / 96.6 / 95.2 % | 93.5 / 97.0 / 95.8 %
n at 30 % pac^1 | 94.0 / 96.3 / 94.5 % | 95.0 / 96.7 / 95.4 % | 95.6 / 97.2 / 95.9 % | 92.8 / 96.5 / 95.1 % | 93.5 / 97.0 / 95.8 % | 94.2 / 97.3 / 96.3 %
n at 50 % Pac.r^1 | 95.2 / 97.3 / 96.3 % | 96.9 / 97.6 / 96.7 % | 96.4 / 97.7 / 97.0 % | 94.3 / 97.5 / 96.5 % | 94.6 / 97.7 / 96.8 % | 94.9 / 97.8 / 97.2 %
n at 75 % Pac.r^1 | 95.6 / 97.7 / 97.0 % | 96.2 / 97.8 /97.3 % | 96.6 / 98.0 / 97.4 % | 94.9 / 97.8 / 97.2 % | 95.0 / 97.9 / 97.4 % | 95.1 / 98.0 / 97.5 %
n at 100 % Pac.r^1 | 95.6 / 97.9 / 97.3 % | 96.2 / 98.0 / 97.5 % | 96.6 / 98.0 / 97.5 % | 95.0 / 98.0 / 97.4 % | 95.1 / 98.0 / 97.5 % | 95.0 / 98.0 / 97.6 %
MPP adaptation efficiency |  |  | > 99.9 %
And at U mppmin / Udcx/Umpp max
PROTECTIVE DEVICES
DC insulation measurement |  |  | Yes
Overload behaviour |  |  | Operating point shift, power limitation
DC. Disconnection |  |  | Yes
Reverse polarity protection |  |  | Yes
INTERFACES
WLAN / Ethernet LAN |  | Fronius Solar,web,Modbus TCP Sun Spec, Fronius Solar API (JSON)
6 inputs and 4 digital in/out |  | Interface to ripple control receiver
USB (A socket) |  | Datalogging, inverter updata via USB flash drive
2xRS422 ®45socket |  | Fronius Solar Net
Signalling output |  | Energy management (Potential-free relay output)
Datalogger and Webserver |  | Included
External input |  | SO-Meter Interface / Input for overvoltage protection
RS485 |  | Modbus RTU Sun Spec or meter connection
INPUT DATA
Max. input current (1dc max 1 / 1 dc max 2) |  | 27.0 A / 16.5 A |  |  | 33.0 A / 27.0 A
Max. usable input current total |  | 43.5 A |  |  | 51.0 A
Max. array short circuit current (MPP1/MPP2) |  | 40.5 A / 24.8 A |  |  | 49.5 A / 40.5 A
Min. input voltage (Udc min) |  |  | 200V
Feed-in start voltage (Udc start) |  |  | 200V
Nominal input voltage(Udc,r) |  |  | 600V
Max. input voltage (Udc max) |  |  | 1,000V
MPP voltage range(Umpp min - Umpp max) | 270 - 800 V | 320 - 800 V |  | 370 - 800V | 420 - 800V
Number MPP trackers |  |  | 2
Number of DC connection |  |  | 3+3
Max. PV generator output (Pdc max) | 15.0KW (peak) | 18.8 KW (peak) | 22.5KW (Peak) | 26.3KW (peak) | 30.0 KW (peak)
OUTPUT DATA
AC nominal output (Pac,r) | 10,000W | 12,500W | 15,000W | 17,500 W | 20,000W
Max. output power | 10,000VA | 12,500VA | 15,000VA | 17,500VA | 20,000VA
AC output current (Iac mom) | 14.4 A | 18.0 A | 21.7 A | 25.3 A | 28.9 A
Grid connection (voltage range) |  | 3 NPE 400V / 230 V or 3-NPE 380 V / 220 V (+20% / 30%)
Frequency (Frequency range) |  | 50 Hz / 60 Hz (45 - 65 Hz)
Total harmonic distortion | 1.8% | 20% | 1.5% | 1.5% | 1.3%
Power factor (cos fay ac,r) |  |  | 0 - 1 ind, / cap.