## Sheet1
Technical Data | GW100K-HT | GW110K-HT | GW120K-HT | GW136K-HTH
PV String Input Data
Max. DC Input Power (kW) | 150 165 180 205
Max. DC Input Voltage (V) | 1100 1100 1100 1100
MPPT Range (V) | 180~1000 180~1000 180~1000 180~1000
Min. Start-up Voltage (V) | 200 | 200 | 200 | 200
Nominal DC Input Voltage (V) | 600 600 600 750@500VAC; 800@540VAC
Max. Input Current (A | 10*30A 10*30A 12*30A 12*30A
Max. Short Current (A) | 10*45A 10*45A 12*45A 12*45A
No. of MPP Trackers | 10 | 10 | 12 | 12
No. of Input Strings per Tracker | 2 | 2 | 2 | 2
AC Output Data
Nominal Output Power (kW) | 100 110 120 136
Max. Output Power (kW) | 110 121 132 150
Max. Output Apparent Power (kVA) | 110 121 132 150
Nominal Output Voltage (V) | 400, 3L/N/PE or 3L/PE | 400, 3L/N/PE or 3L/PE | 400, 3L/N/PE or 3L/PE | 400, 3L/N/PE or 3L/PE
Nominal Ouput Frequency (Hz) | 50/60 | 50/60 | 50/60 | 50/60
Max. Output Current (A) | 167 175.5 191.3 173.2A@ 500V; 160.4A@540V
Output Power Factor |  | ~1 (Adjustable from 0.8 leading to 0.8 lagging)
Output THDi (@Nominal Output) | <3% | <3% | <3% | <3%
Efficiency
Max. Efficiency | 98.6% | 98.6% | 98.6% | 98.6%
European Efficiency | 98.3% | 98.3% | 98.3% | 98.3%
Protection
PV String Current Monitoring | Integrated | Integrated | Integrated | Integrated
Internal Humidity Detection | Integrated | Integrated | Integrated | Integrated
Insulation Resistor Detection | Integrated | Integrated | Integrated | Integrated
Residual Current Monitoring | Integrated | Integrated | Integrated | Integrated
Anti-islanding Protection | Integrated | Integrated | Integrated | Integrated
Input Reverse Polarity Protection | Integrated | Integrated | Integrated | Integrated
DC SPD Protection |  | Type II (Type I optional)
AC SPD Protection |  | Type II (Type I optional)
Output Over Current Protection | Integrated | Integrated | Integrated | Integrated
Output Short Protection | Integrated | Integrated | Integrated | Integrated
Output Over Voltage Protection | Integrated | Integrated | Integrated | Integrated
Arc Fault Protection | Optional | Optional | Optional | Optional
Emergency Power off | Optional | Optional | Optional | Optional
AC Terminal Over-temperature Protection | Optional | Optional | Optional | Optional
PID Recovery | Optional | Optional | Optional | Optional
General Data
Operating Temperature Range C | '-30 ~ 60 | '-30 ~ 60 | '-30 ~ 60 | '-30 ~ 60
Relative Humidity | 0 ~ 100% | 0 ~ 100% | 0 ~ 100% | 0 ~ 100%
Operating Altitude | <=4000 | <=4000 | <=4000 | <=4000
Cooling | Fan cooling | Fan cooling | Fan cooling | Fan cooling
User Interface |  | LCD, Bluetooth +APP (LCD optional)
Communication | RS485 or PLC or Wifi | RS485 or PLC or Wifi | RS485 or PLC or Wifi | RS485 or PLC or Wifi
Weight (Kg) | 88.5 | 88.5 | 88.5 | 88.5
Dmension (Width*Height*Depth mm) | 1005*676*340 | 1005*676*340 | 1005*676*340 | 1005*676*340
Protection Degree | IP66 | IP66 | IP66 | IP66
Night Self Consumption (W) | < 2 | < 2 | < 2 | < 2
Topology |  | Transformerless