## Sheet1
Technical Data | GW4000-DT | GW5000-DT | GW6000-DT | GW8000-DT | GW10KN-DT | GW12KN-DT | GW15KN-DT
PV String Input Data
Max.DC Input Power (W) | 5200 | 6500 | 7800 | 9600 | 12000 | 16800 | 19500
Max.DC Input Voltage (V) | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
MPPT Range(V) | 200~800 | 200~800 | 200~800 | 200~850 | 200~850 | 200~850 | 200~850
Start-up Voltage(V) | 180 | 180 | 180 | 180 | 180 | 180 | 180
MPPT Range for Full Load(V) | 195~800 | 240~800 | 285~800 | 380~850 | 480~850 | 380~580 | 480~850
Nominal DC Input Voltage(V) | 620 | 620 | 620 | 620 | 620 | 620 | 620
Max.Input Current (A) | 11/11 | 11/11 | 11/11 | 11/11 | 11/11 | 22/11 | 22/11
Max.Short Current (A) | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 27.6/13.8 | 27.6/13.8
No.of MPP Trackers | 2 | 2 | 2 | 2 | 2 | 2 | 2
No.of Input String per Tracker | 1/1 | '1/1 | '1/1 | '1/1 | '1/1 | '1/1 | '1/1
AC Output Data
Nominal Output power(W) | 4000 | 5000 | 6000 | 8000 | 10000 | 12000 | 15000
Max.Output Power(W) | 4000 | 5000 | 6000 | 8000 | 10000 | 12000 | 15000
Nominal Output voltage(V) | 400, 3L/N/PE | 400, 3L/N/PE | 400, 3L/N/PE | 400, 3L/N/PE | 400, 3L/N/PE | 400, 3L/N/PE | 400, 3L/N/PE
Nominal Output Frequency(Hz) | 50/60 | 50/60 | 50/60 | 50/60 | 50/60 | 50/60 | 50/60
Max.Output Current(A) | 8.5 | 8.5 | 10 | 12.1 | 15.2 | 21.5 | 24
Output Power Factor |  |  | ~1(Adjustable form 0.8leading to 0.8lagging)
Output THDi @ Nominal Output | <2% | <2% | <2% | <2% | <2% | <2% | <2%
Efficiency
Max.Efficiency | 98% | 98% | 98% | 98.3% | 98.3% | 98.3% | 98.3%
Euro Efficiency | 97.5% | 97.5% | 97.5% | 98% | 98% | 98% | 98%
MPPT Efficiency | 99.9% | 99.9% | 99.9% | 99.9% | 99.9% | 99.9% | 99.9%
Protection
Anti-islanding Protection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
Input Reverse Polarity Protection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
Insulation Resistor detection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
Residual Current Monitoring Unit | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
Output Over current Protection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
Output short protection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
Output over voltage Protection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
General Data
Operating Temperature Range© | -25~60 | '-25~60 | '-25~60 | '-25~60 | '-25~60 | '-25~60 | '-25~60
Relative Humidity | 0~100% | 0~100% | 0~100% | 0~100% | 0~100% | 0~100% | 0~100%
Operating Altitude(m) | <=4000 | <=4000 | <=4000 | <=4000 | <=4000 | <=4000 | <=4000
Cooling |  |  |  | Natural Convection
Noise(db) | <30 | <30 | <30 | <30 | <30 | <30 | <30
User Interface | LCD & LCD | LCD & LCD | LCD & LCD | LCD & LCD | LCD & LCD | LCD & LCD | LCD & LCD
Communication | RS485 or WiFi | RS485 or WiFi | RS485 or WiFi | RS485 or WiFi | RS485 or WiFi | RS485 or WiFi | RS485 or WiFi
Weight(Kg) | 24 | 24 | 24 | 24 | 24 | 24 | 24
Size (Width*Height*Depthmm) | 516*455*192 | 516*455*192 | 516*455*192 | 516*455*192 | 516*455*192 | 516*455*192 | 516*455*192
Protection Degree | IP65 | IP65 | IP65 | IP65 | IP65 | IP65 | IP65
Night Self Consumption(W) | <1 | <1 | <1 | <1 | <1 | <1 | <1
Topology | Transformerless | Transformerless | Transformerless | Transformerless | Transformerless | Transformerless | Transformerless
Standards
Safety Regulation |  |  |  | IEC62109-1&2
EMC |  |  |  | EN61000-6-1, EN61000-6-3, EN61000-6-4

## Sheet2
Easy wall mounting
Super large 5-inch LCD
RS485 and Wi-Fi communication
IP65 dustproof and waterproof
Fanless and quiet