## Sheet1
Technical Data | GW17K-DT | GW20K-DT | GW25K-DT
PV String Input Data
Max.DC Input Power(W) | 22100 | 26000 | 32500
Max.DC Input Voltage(V)* | 1000 | 1000 | 1000
MPPT Range (V) | 260~850 | 260~850 | 260~850
Start-up Voltage(V) | 250 | 250 | 250
MPPT Range for Full Load(V) | 400~850 | 470~850 | 480~850
Nominal DC Input voltage(v) | 620 | 620 | 620
Max.Input Current (A) | 22/22 | 22/22 | 27/27
Max.Short Current (A) | 27.5/27.5 | 27.5/27.5 | 33.8/33.8
No. of MPP Trackers | 2 | 2 | 2
No.of Input Strings per Tracker | 2 | 2 | 3
AC Output Data
Nominal Output Power(W) | 17000 | 20000 | 2500
Max. Output Apparent power(VA) | 17000 | 20000 | 2500
Nominal Output Voltage (V) | 400,3L/N/PE | 400,3L/N/PE | 400,3L/N/PE
Nominal Output Frequency(Hz) | 50/60 | 50/60 | 50/60
Max.Output Current(A) | 25 | 30 | 37
Output power Factor |  | ~1(adjustable from 0.8 leading to 0.8 Lagging)
Output THDi (@ Nominal Output) | <1.5% | <1.5% | <1.5%
Efficiency
Max.Efficency | 98.2% | 98.4% | 98.4%
Europe Efficiency | 97.7% | 98.1% | 98.1%
MPPT Efficiency | 99.9% | 99.9% | 99.9%
Protection
Anti-islanding protection | Integrated | Integrated | Integrated
Input Reverse polarity protection | Integrated | Integrated | Integrated
Insulation Resistor Detection | Integrated | Integrated | Integrated
DC SPD Protection | Integrated | Integrated | Integrated
Residual Current Monitoring Unit | Integrated | Integrated | Integrated
Output Over Current Protection | Integrated | Integrated | Integrated
Output Short Protection | Integrated | Integrated | Integrated
Output Over voltage protection | Integrated | Integrated | Integrated
General Data
Operating Temperature Range © | -25~60 | -25~60 | -25~60
Relative Humidity | 0~100% | 0~100% | 0~100%
Operating Altitude(m) | <=4000 | <=4000 | <=4000
Cooling | Fan Cooling | Fan Cooling | Fan Cooling
Noise(dB) | <45 | <45 | <45
User interface | LCD & LED | LCD & LED | LCD & LED
Communication | RS485 or WiFi | RS485 or WiFi | RS485 or WiFi
Weight(Kg) | 39 | 39 | 40
Size (Width*Height*Depth mm) | 516*650*203mm | 516*650*203mm | 516*650*203mm
Protection Degree | IP65 | IP65 | IP65
Night Self Consumption (W) | <1 | <1 | <1
Topology | Transformerless | Transformerless | Transformerless
Certification & Standards
Grid regulation | VDE0126-1-1,VDE-AR-N4105 AS4777.2,G83/2,EN50438(PL),EN50438(SW),EN50438(IR),NRS097-2-1,ERDF-NOI-RES-13E,IEC61727,IEC62116 | VDE0126-1-1,VDE-AR-N4105 AS4777.2,G83/2,EN50438(PL),EN50438(SW),EN50438(IR),NRS097-2-1,ERDF-NOI-RES-13E,IEC61727,IEC62116 | VDE0126-1-1,VDE-AR-N4105 AS4777.2,G83/2,EN50438(PL),EN50438(SW),EN50438(IR),NRS097-2-1,ERDF-NOI-RES-13E,IEC61727,IEC62116
safety Regulation | IEC62109-1&2 | IEC62109-1&2 | IEC62109-1&2
EMC |  | EN61000-6-1,EN61000-6-2,EN61000-6-3,EN61000-6-4