## Sheet1
Technical Data | GW25K-MT | GW30K-MT | GW36K-MT
DC Input Data
Max. PV Power (W) | 32500 | 39000 | 42900
Max. DC Input Voltage | 1100 | 1100 | 1100
MPPT Range (V) | 200~900 | 200~900 | 200~900
Starting Voltage (V) | 180 | 180 | 180
Nominal DC Input Voltage (V) | 600 | 600 | 600
Max. Input Current (A) | 25/25/25 | 25/25/25 | 25/25/25
Max. Short Current (A) | 31.1/31.1/31.1
No. of MPP Trackers | 3 | 3 | 3
No. of Input Strings per Tracker | 2/2/2 | '2/2/2 | '2/2/2
AC Output Data
Nominal Output Power (W) | 25000 | 30000* | 36000
Max. Output Power (W) | 27500 | 33000* | 36000
Max. Output Apparent Power (VA) | 27500 | 33000* | 36000
Nominal Output Voltage (V) |  | 400, 3L/N/PE or 3L/PE
Nominal Output Frequency (Hz) | 50/60 | 50/60 | 50/60
Max. Output Current (A) | 40 | 48 | 53.3
Output Power Factor |  | ~1(Adjustable from 0.8 leading to 0.8 Lagging)
Output THDi @ (Nominal Output) | <3% | <3% | <3%
Efficiency
Max. Efficiency | 96.7% | 98.8% | 98.8%
European Efficiency | >98.4% | >98.5% | >98.5%
Protection
Anti-Islanding Protection | Integrated | Integrated | Integrated
Input Reverse Polarity Protection | Integrated | Integrated | Integrated
PV String Current Monitoring | Integrated | Integrated | Integrated
Anti-PID Function for Module | Optional | Optional | Optional
Insulation monitoring | Integrated | Integrated | Integrated
DC SPD Protection | Optional (Type II) | Optional (Type II) | Optional (Type II)
DC SPD Protection | Optional (Type II) | Optional (Type II) | Optional (Type II)
Residual Current Monitoring Unit | Integrated | Integrated | Integrated
AC Over Current Protection | Integrated | Integrated | Integrated
AC Short Protection | Integrated | Integrated | Integrated
AC Over Voltage Protection | Integrated | Integrated | Integrated
General Data
Ambient Temperature Range© | -30~60 | '-30~60 | '-30~60
Relative Humidity | 0~100% | 0~100% | 0~100%
Operating Altitude (m) | <3000 | <3000 | <3000
Cooling | Fan Cooling | Fan Cooling | Fan Cooling
Display |  | LCD & LED or APP & LED
Communication | RS485 or WiFi or GPRS or PLC (LCD); WiFi+RS485 or GPRS +nRS485(APP)
Weight(kg) | 40 | 40 | 40
Dimension (width*Height*Depth mm) | 480*590*200 | 480*590*200 | 480*590*200
Protection Degree | IP65 | IP65 | IP65
Night Self Consumption (W) | <1 | <1 | <1
Topology |  | ransformerles
Certifications & Standards
Grid Regulation |  | AS4777.2/VDE0126-1-1/VDE-AR-N4105
Safety Regulation |  | IEC62109-1&-2
EMC Regulation |  | EN61000-6-1/EN61000-6-2/EN61000-6-3/EN61000-6-4