## Sheet1
Technical Data | GW4000-SDT-20 | GW5000-SDT-20 | GW6000-SDT-20 | GW8000-SDT-20 | GW10K-SDT-20 | GW12K-SDT-20 | GW12KVL-SDT-20 | GW15K-SDT-20 | GW17K-SDT-20 | GW20K-SDT-20
Input
Max. Input Voltage (V) | 1000 | 1000 | 1000 | 1100 | 1100 | 1100 | 800 | 1100 | 1100 | 1100
MPPT Operating Voltage Range | 180 ~ 850 | 180 ~ 850 | 180 ~ 850 | 140 ~ 950 | 140 ~ 950 | 140 ~ 950 | 140 ~ 650 | 140 ~ 950 | 140 ~ 950 | 140 ~ 950
Start-up Voltage(V) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
Nominal Input Voltage(V) | 620 | 620 | 620 | 620 | 620 | 620 | 620 | 620 | 620 | 620
Max. Input Current per MPPT(A) | 16 | 16 | 16 | 15 | 15 | 30 | 30 | 30 | 30 | 30
Max. Short Circuit Current per MPPT | 20 | 20 | 20 | 18.7 | 18.7 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Number of MPP trackers | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Number of Strings per MPPT | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2
Output
Nominal Output Power (W) | 4000 | 5000 | 6000 | 8000 | 10000 | 12000 | 12000 | 15000 | 17000 | 20000
Nominal Output Apparent Power | 4000 | 5000 | 6000 | 8000 | 10000 | 12000 | 12000 | 15000 | 17000 | 20000
Max. AC Active Power(W) | 4400 | 5500 | 6600 | 8800 | 11000 | 13200 | 12000 | 16500 | 18700 | 22000
Max. AC Apparent Power(VA) | 4400 | 5500 | 6600 | 8800 | 11000 | 13200 | 12000 | 16500 | 18700 | 22000
Nominal Output Voltage(V) | 400, 3L / N / PE |  | 380 / 400 / 415 , 3L / N / PE |  |  | 220 / 127, 3L / N / PE |  | 380 / 400 / 415, 3L / N / PE
Output Voltage Range(V) | 180 ~ 270 | 180 ~ 270 | 180 ~ 270 | 180 ~ 270 | 180 ~ 270 | 180 ~ 270 | 180 ~ 270 | 180 ~ 270 | 180 ~ 270 | 180 ~ 270
Nominal AC Grid Frequency(Hz) | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60
AC Grid Frequency Range (Hz) |  |  |  |  | 45 ~ 55 / 55 ~ 65
Max. Output Current (A) | 6.4 | 8 | 9.6 | 12.8 | 16 | 19.1 | 31.9 | 24 | 27.1 | 32
Power Factor |  |  |  | ~ 1 (Adjustable from 0.8 leading to 0.8 lagging)
Max. Total Harmonic Distortion | <3% | <3% | <3% | <3% | <3% | <3% | <3% | <3% | <3% | <3%
Efficiency
Max. Efficiency | 98.2% | 98.2% | 98.2% | 98.3% | 98.3% | 98.4% | 96.9% | 98.4% | 98.4% | 98.4%
European Efficiency | 97.6% | 97.6% | 97.6% | 97.6% | 97.6% | 97.8% | 96.4% | 97.8% | 97.8% | 97.8%
Protection
PV Insulation Resistance Detection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
Residual Current Monitoring | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
PV Reverse Polarity Protection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
Anti-islanding Protection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
AC Overcurrent Protection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
AC Short Circuit Protection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
AC Overvoltage Protection | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
DC Switch | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated | Integrated
DC Surge Protection |  |  |  |  | Type III (Type II Optional)
AC Surge Protection |  | Type III |  |  |  |  | Type III (Type II Optional)
AFCI | Optional | Optional | Optional | Optional | Optional | Optional | Optional | Optional | Optional | Optional
Emergency Power Off | Optional | Optional | Optional | Optional | Optional | Optional | Optional | Optional | Optional | Optional
Remote Shutdown | Optional | Optional | Optional | Optional | Optional | Optional | Optional | Optional | Optional | Optional
General Data
Operating Temperature Range© | -30 ~ +60 | '-30 ~ +60 | '-30 ~ +60 | '-30 ~ +60 | '-30 ~ +60 | '-30 ~ +60 | '-30 ~ +60 | '-30 ~ +60 | '-30 ~ +60 | '-30 ~ +60
Relative Humidity | 0 ~ 100% | 0 ~ 100% | 0 ~ 100% | 0 ~ 100% | 0 ~ 100% | 0 ~ 100% | 0 ~ 100% | 0 ~ 100% | 0 ~ 100% | 0 ~ 100%
Max. Operating Altitude (m) | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
Cooling Method |  | Natural Convection | [5 empty] | Smart Fan Cooling
Display |  |  |  | LED, LCD (Optional), WLAN + APP
Communication |  |  |  | WiFi, RS485 or LAN or 4G (Optional)
Weight (Kg) | 15 | 15 | 15 | 20.5 | 20.5 | 20.5 | 26 | 26 | 26 | 26
Dimension (W x H x D mm) |  | 354 x 433 x 147 |  | 415 x 511 x 175 |  |  |  | 415 x 511 x 198
Noise Emission(dB) | <34 | <34 | <34 | <25 | <25 | <50 | <50 | <50 | <50 | <50
Topology |  |  |  |  | Non-isolated
Self-consumption at Night (W) | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
Ingress Protection Rating | IP65 | IP65 | IP65 | IP65 | IP65 | IP65 | IP65 | IP65 | IP65 | IP65
DC Connector |  |  |  |  | MC4(4 ~ 6mm^2)
AC Connector |  |  | Plug and play connector |  |  |  |  | OT Terminal