## Sheet1
Datasheet | MAX 100KTL3-X LV | MAX 110KTL3-X LV | MAX 120KTL3-X LV | MAX 125KTL3-X LV
Input data (DC)
Max. Dc voltage |  | 1100V
Start voltage |  | 195V
Nominal voltage |  | 600V
MPP voltage range |  | 180V-1000V
No. of MPP trackers |  | 10
No. of PV strings per MPP tracker |  | 2
Max. input current per MPP tracker |  | 32A
Max. short-circuit current per MPP tracker |  | 40A
Output data (AC)
AC nominal power | 100000W | 110000W | 120000W | 125000W
Max. AC apparent power | 110000VA | 121000V | 132000VA | 137500VA
Nominal AC voltage(range*) |  | 230V/400V(340-440VAC)
AC grid grid frequency (range*) |  | 50/60 Hz(45 ~ 55Hz/55 - 65 Hz)
Max. output current | 158.8A | 174.6A | 190.5A | 198.5A
Adjustable power factor |  | 0.8leading … 0.8lagging
THDi |  | <3%
AC grid connection type |  | 3W/N/PE
Efficiency
Max.efficiency |  | 98.8%
European efficiency | 98.4% | 98.5% | 98.5% | 98.5%
MPPT efficiency |  | 99.9%
Protection devices
DC reverse polarity protection |  | Yes
DC switch |  | Yes
AC/DC surge protection |  | Type II / Type II
Insulation resistance monitoring |  | Yes
AC short-circuit protection |  | Yes
Ground fault monitoring |  | Yes
String detection |  | Yes
Anti PID function |  | Opt
Arc fault detection[AFCI] |  | Opt
General data
Dimensions (W / H / D) |  | 970/640/345mm
Weight |  | 48Kg
Operating temperature range |  | -30C…+60C
Nighttime power consumption |  | < 1W
Topology |  | Transformerless
Cooling |  | Smart Cooling
Protection Degree |  | IP66
Relative humidity |  | 0 ~ 100%
Altitude |  | 4000m
DC connection |  | H4/MC4 [Max.6mm^2)
AC connection |  | OT Terminal [Max. 240mm^2)
Display |  | LED/WiFi+APP
Interfaces: RS485/USB/PLC/GPRS/4G/WiFi |  | Yes/Yes/Optional/Optional/Optional/Optional
Warranty:5 years / 10 years |  | Yes/Optional

## Sheet2
10 MPPTs fusefree design
Smart I/V scan and diagnosis
Intelligent string monitoring
AC&DC type II SPD
IP66 and C5 protection