## Sheet1
Datasheet | MOD 10KTL3-X | MOD 11KTL3-X | MOD 12KTL3-X | MOD 13KTL3-X | MOD 15KTL3-X
Input data (DC)
Max. recommended PV power | 15000W | 16500W | 18000W | 19500W | 22500W
Max. DC voltage |  |  | 1100V
Start voltage |  |  | 160V
Nominal voltage |  |  | 580V
MPPT voltage range |  |  | 140V-1000V
No. of MPP trackers |  |  | 2
No. of PV strings per MPP trackers | 1 | 1 | 1/2 | '1/2 | '1/2
Max. input current per MPP tracker | 13 A | 13A | 13/26A | 13/26A | 13/26A
Max. short-circuit current per MPP tracker | 16A | 16A | 16/32A | 16/32A | 16/32A
Output data (AC)
AC nominal power | 10000W | 11000W | 12000W | 13000W | 15000W
Max. AC apparent power | 11000VA* | 12100VA | 13200VA | 14300VA | 16500VA
Nominal AC voltage (range*) |  |  | 220 V / 380V, 230V/400V (340-440)
AC grid frequency (range*) |  |  | 50/60 Hz (45-55Hz/55-65 Hz)
Max. output current | 16.7A | 18.3A | 20A | 21.7A | 25A
Adjustable power factor |  |  | 0.8leading…0.8lagging
THDi |  |  | <3%
AC grid connection type |  |  | 3W + N + PE
Efficiency
MAX. efficiency |  |  | 98.6%
European efficiency | 98.1% | 98.1% | 98.2% | 98.2% | 98.2%
MPPT efficiency |  |  | 99.9%
Protection devices
DC reverse polarity protection |  |  | Yes
DC Switch |  |  | Yes
AC/DC surge protection |  |  | Type II / Type II
Insulation resistance monitoring |  |  | Yes
AC short-circuit protection |  |  | Yes
Ground fault monitoring |  |  | Yes
Grid monitoring |  |  | Yes
Anti-islanding protection |  |  | Yes
Residual-current monitoring unit |  |  | Yes
String fault monitoring |  |  | Yes
AFCI protection |  |  | Optional
General data
Dimensions(W/H/D) |  |  | 425/387/178mm
Weight | 14Kg | 14Kg | 16Kg | 16Kg | 16Kg
Operating temperature range |  |  | -25C … +60C
Nighttime power consumption |  |  | < 1W
Topology |  |  | Transformerless
Cooling |  |  | Natural convection
Protection degree |  |  | IP66
Relative humidity |  |  | 0 ~ 100%
Altitude |  |  | 4000m
DC connection |  |  | H4/MC4(Optional)
AC connection |  |  | Connector
Display |  |  | OLED+LED/WiFi+APP
Interfaces: USB/RS485/WiFi/GPRS/LAN/RF |  | yes/yes/Optional/Optional/Optional/Optional
Warranty:5 / 10 years |  |  | Yes/Optional