## Sheet1
Datasheet | MAX 185KTL3-X-HV | MAX 216KTL3-X HV | MAX 250KTL3-X HV | MAX 253KTL3-X-HV
Input data (DC)
Max.DC power | 277.5KW | 324KW | 375KW | 378.5KW
Max. DC Voltage |  | 1500V
Start voltage |  | 1500V
Nominal voltage |  | 1080V
MPP voltage range |  | 500V-1500V
No. of MPP trackers | 9 | 9 | 12 | 15
No. of PV strings per MPP trackers |  | 2
Max. input current per MPP tracker |  | 30A
Max. short-circuit current per MPP tracker |  | 50A
Output data (AC)
AC nominal power | 185KW | 216KW | 250KW | 253KW
Max. AC apparent power | 185KVA@30C, 175KVA@40C, 160KVA@50C | 216KVA@30C, 200KVA@40C, 192KVA@50C | 250KVA@30C, 230KVA@45C, 220KVA@50C | 253KVA@30C, 230KVA@45C, 220KVA@50C
Nominal AC voltage (range*) |  | 800V (640-920V)
AC grid frequency (range*) |  | 50/60 Hz(45-55Hz/55-65 Hz)
Max. output current | 133.5A | 155.9A | 180.4A | 182.6A
Adjustable power factor |  | 0.8leading…0.8lagging
THDi |  | <3%
AC grid connection type |  | 3W+PE
Efficiency
Max.efficiency |  | 99%
European efficiency | 98.7% | 98.7% | 98.7% | 98.5%
MPPT efficiency |  | 99.9%
Protection devices
DC reverse polarity protection |  | Yes
DC switch |  | Yes
AC/AC surge protection |  | Type II / Type II
Insulation resistance monitoring |  | Yes
AC short-circuit protection |  | Yes
Ground fault monitoring |  | Yes
Grid monitoring |  | Yes
Anti-islanding protection |  | Yes
Residual-current monitoring unit |  | Yes
String monitoring |  | Yes
AFCI protection |  | Optional
Anti-PID function |  | Optional
LVRT |  | Yes
HVRT |  | Yes
Night SVG |  | Optional
General data
Dimensions(W/H/D) |  | 1070/675/340mm
Weight | 95Kg | 95Kg | 99Kg | 109Kg
Operating temperature range |  | -30C … +60C
Nighttime power consumption |  | < 1W
Topology |  | Transformerless
Cooling |  | Smart air cooling
Protection degree |  | IP66
Relative humdity |  | 0-100%
Altitude |  | 4000m
DC Connection |  | Staubi MCA/Amphenol UTX
AC Connection |  | OT Terminal connectors (Max. 300mm^2)
Display |  | LED/WiFi +APP
Interfaces:RS485/USB/PLC/4G/GPRS |  | Yes/Yes/Optional/Optional/Optional
Warranty: 5 years / 10 years |  | Yes/Optional