## Sheet1
Datasheet | MID 15KTL3-X | MID 17KTL3-X | MID 20KTL3-X | MID 22KTL3-X | MID 25KTL3-X
Input data (DC)
Max.recommended PV Power(for module STC) | 22500W | 25500W | 30000W | 33000W | 37500W
Max. DC voltage |  |  | 1100V
Start voltage |  |  | 250V
Nominal voltage |  |  | 580V
MPPT voltage range |  |  | 160V - 1000V
No. of MPP trackers |  |  | 2
No. of PV strings per MPP tracker | 2 | 2 | 2 | 2 | 2
Max. input current per MPPT tracker | 25A | 25A | 25A | 25A | 25A/37.5A
Max. short circuit current per MPPT | 32A | 32A | 32A | 32A | 32A/48A
Output data (AC)
Rated AC output Power | 15000W | 17000W | 20000W | 22000W | 25000W
Max. AC apparent power | 16600VA | 18800VA | 22000VA | 24400VA | 27700VA
Nominal AC voltage (range*) |  | 220/380V, 230V/400V (340-440V)
AC grid frequency(range*) |  | 50/60 Hz (45-55Hz/55-65 Hz)
Max. output current | 24.2A | 27.4A | 31.9A | 35.5A | 40.2A
Adjustable power factor |  | 0.8leading…0.8lagging
THDi |  | <3%
AC grid connection type |  | 3W+N+PE
Efficiency
Max. efficiency |  | 98.75%
European efficiency |  | 98.6%
MPPT efficiency |  | 99.9%
Protection devices
DC reverse polarity protection |  | Yes
DC Switch |  | Yes
AC/DC surge protection |  | TypeII/Type II
Insulation resistance monitoring |  | Yes
AC short-circuit protection |  | Yes
Ground fault monitoring |  | Yes
Grid monitoring |  | Yes
Antislanding protection |  | Yes
Residual-current monitoring unit |  | Yes
String monitoring |  | Optional
AFCI protection |  | Optional
General data
Dimensions [w /H / D] |  | 525/395/222mm
Weight |  | 23kg
Operating temperature range |  | -25C…+60C
Noise emission (typical) |  | <=40 dB(A)
Self-Consumption (night) |  | <1W
Topology |  | Transformerless
Cooling |  | Smart air cooling
Protection degree |  | IP65
Relative Humidity |  | 0 ~ 100%
Altitude |  | 4000m
DC connection |  | H4/MC4(Optional)
AC connection |  | Cable gland + OT terminal
Display |  | OLED+LED/WiFi+APP
Interfaces: RS485 / USB / WiFi / GPRS / RF / LAN |  | Yes/Yes/Optional/Optional/Optional/Optional
Warranty: 5 years / 10 years |  | Yes/Optional

## Sheet2
Max. efficiency 98.7%
40% compact and lighter
Dual MPP trackers
Supports export control
Touch ke and OLED display
Type II SPD on AC and DC side
Data storage up to 25 years
DC side 2 in 1 connection enabled