## Sheet1
Datasheet | MAC 30KTL3-X LV | MAC 40KTL3-X LV | MAC 50KTL3-X LV | MAC 60KTL3-X LV
Input data (DC)
Max. recommended PV | 45000W | 6000W | 75000W | 9000W
Maax. DC voltage |  | 1100V
Start voltage |  | 250V
Nominal voltage |  | 600V
MPPT voltage range |  | 200V - 1000V
No. of MPP trackers |  | 3
No. of PV strings per MPP tracker | 3/3/2 | 3/3/3 | 4/3/3 | 4/4/4
Max. input current per MPP tracker | 37.5A/37.5A/25A | 37.5A/37.5A/37.5A | 50A/37.5A/37.5A | 50A/50A/50A
Max.short-circuit current | 45A | 45A | 55A | 55A
Output data (AC)
Rated AC output power | 30000 | 40000 | 50000 | 60000
Max. AC apparent power | 33300VA | 44400VA | 55500VA | 66600VA
Nominal AC voltage (range*) |  | 230V/400V (340-440V)
AC grid frequency (range*) |  | 50/60 Hz (45-55Hz/55-65Hz)
Max. output current | 48.3A | 64.4A | 80.5A | 96.6A
Adjustable power factor |  | 0.8leading…0.8lagging
THDi |  | <3%
AC grid connection type |  | 3W+N+PE
Efficiency
Max. efficiency | 98.7% | 98.7% | 98.7% | 98.8%
European efficiency | 98.4% | 98.5% | 98.5% | 98.5%
MPPT efficiency |  | 99.9%
Protection devices
DC reverse polarity protection |  | Yes
DC switch |  | Yes
AC/DC surge protection |  | Type II / Type II
Insulation resistance monitoring |  | Yes
AC short-circuit protection |  | Yes
Ground fault monitoring |  | Yes
Grid monitoring |  | Yes
Anti-islanding protection |  | Yes
Residual-current monitoring unit |  | Yes
General data
Dimensions(W / H / D) |  | 680/508/281mm
Weight |  | 52Kg
Operating temperature range |  | -25C…+60C
Noise emission(Typical) |  | <=60dB(A)
Nighttime power consumption |  | < 1W
Topology |  | Transformerless
Cooling |  | Smart air cooling
Protection degree |  | IP65
Relative humidity |  | 0 ~ 100%
Altitude |  | 4000m
DC Connection |  | H4/MC4 (Optional)
AC Connection |  | Cable gland + OT terminal
Display |  | OLED+LED/WiFi+APP
Interfaces:RS485 / USB /WiFi/GPRS / RF |  | Yes/Yes/Optional/Optional/Optional
Warranty:5 years / 10 years |  | Yes/Optional

## Sheet2
3 MPPTs
Smart diagnosis
High efficiency up to 98.8%
Local WIFI connection
OLED display and touch button
AC&DC type II SPD
Data storage up to 25 years
DC side 2 in 1 connection enabled