## Sheet1
Datasheet | MAX 50KTL3 LV | MAX 60KTL3 LV | MAX 70KTL3 LV | MAX 70KTL3 LV2
Input data(DC)
Max. recommended PV Power(for module STC) | 75000W | 90000W | 105000W | 120000W
Max. DC Voltage |  | 1100V
Start Voltage |  | 250V
Nominal voltage | 585V | 585V | 600V | 600V
MPPT voltage range |  | 200V-1000V
No. of MPP trackers | 6 | 6 | 7 | 7
No. of PV strings per MPP tracker |  | 2
Max. input current per MPP tracker |  | 26A
Max. short-circuit current Per MPP tracker |  | 32A
Output data (AC)
AC nominal power | 50000W | 60000W | 70000W | 80000W
Max. AC apparent power | 55500VA | 66600VA | 77700VA | 88800VA
Nominal AC voltage (range*) |  | 220/380V, 230V/400V (340-440)
AC grid frequency (range*) |  | 50/60 Hz (45-55Hz/55-65 Hz)
Max. output current | 80.5A | 96.6A | 112.7A | 128.8A
Adjustable power factor |  | 0.8leading … 0.8lagging
THDi |  | <3%
AC grid connection type |  | 3W+N+PE
Efficiency
Max.efficiency | 98.8% | 98.8% | 99% | 99%
European efficiency | 98.4% | 98.4% | 98.5% | 98.5%
MPPT efficiency |  | 99.9%
Protection devices
DC reverse polarity protection |  | Yes
DC switch |  | Yes
DC surge protection |  | Type II / Type II
Insulation resistance monitoring |  | Yes
AC short-circuit protection |  | Yes
Ground fault monitoring |  | Yes
Grid monitoring |  | Yes
Anti-islanding protection |  | Yes
Residual-current monitoring unit |  | Yes
String monitoring |  | Yes
AFCI protection |  | Optional
General data
Dimensions (W / H / D) |  | 860/600/300mm
Weight | 82Kg | 82Kg | 86Kg | 86Kg
Operating temperature range |  | -25C … +60C
Self-consumption |  | < 1W
Topology |  | Transformerless
Cooling |  | Smart air cooling
Protection degree |  | IP65
Relative humidity |  | 0-100%
Altitude |  | 4000m
DC connection |  | H4/MC4(Optional)
AC connection |  | Cable gland+OT terminal
Display |  | LED/WIFI+APP
Interfaces: RS485 / USB / WiFi/RF/GPRS |  | Yes/Yes/Optional/Optional/Optional
Warranty: 5 years / 10 years |  | Yes/Optional

## Sheet2
6 /7MPPTs, fusefree design
High efficiency up to 99%
One-click diagnosis
String monitoring
AC&DC type II SPD
AFCI optional