## Sheet1
Technical Specification | SUN2000-12KTL-M5 | SUN2000-15KTL-M5 | SUN2000-17KTL-M5 | SUN2000-20KTL-M5 | SUN2000-25KTL-M5
Efficiency
Max. efficiency | 98.4% | 98.4% | 98.4% | 98.4% | 98.4%
European weighted efficiency | 97.9% | 98% | 98.1% | 98.1% | 98.2%
Input
Recommended max PV power | 18,000 Wp | 22,500 Wp | 25,500 Wp | 30,000 Wp | 37,500 Wp
Max. input voltage^2 |  |  | 1100V
Full-Load MPPT voltage range | 370 ~ 800V | 410 ~ 800 V | 440 ~ 800 V | 480 ~ 800V | 530 ~ 800 V
MPPT operating voltage range^3 |  |  | 200 ~ 1000V
Start-up voltage |  |  | 200 V
Rated input voltage |  |  | 600 V
Max. input current per MPPT |  | 30 A (two-string)/20 A (single string)
Max.short-circuit current |  |  | 40 A
Number of MPP trackers |  |  | 2
Max. number of inputs |  |  | 4
Output
Grid connection |  |  | Three-phase
Rated output power | 12,000 W | 15,000 W | 17,000W | 20,000 W | 25,000 W
Max. apparent power | 13,200 W | 16,500 VA | 18,700 VA | 22,000 VA | 27,500 VA
Rated output voltage | 220VAC/380 VAC , 230 V AC/400 VAC/ 239.6 VAC/415VAC, 3W + N + PE
Rated AC grid frequency |  |  | 50 Hz/60 Hz
Max. output current | 18.2 A/380 VAC, 17.3 A/400 VAC, 16.7A/415 VAC | 25.2A/380VAC, 23.9A/400 VAC, 23.1 A/415 VAC | 28.6 A/380 VAC, 31.9 A/400VAC,30.8 A/415 VAC | 33.6 A/380 VAC, 31.9A/400VAC,30.8 A/415 VAC | 42.0 A/380 VAC, 39.9 A/400 VAC, 38.5 A/415VAC
Adjustable power factor |  |  | 0.8leading … 0.8lagging
Max. total harmonic distortion |  |  | <=3%
Protection Feature
Overvoltage category |  |  | PV II / AC III
Input-side disconnection device |  |  | Yes
Anti-islanding protection |  |  | Yes
AC over-current protection |  |  | Yes
DC reverse polarity protection |  |  | Yes
String fault detection |  |  | Yes
DC surge protection |  |  | TYPE II
AC surge protection |  |  | CLASS II
Residual current monitoring unit |  |  | Yes
Arc fault protection |  |  | Yes
Ripple receiver control |  |  | Yes
General Specification
Operating temperature range |  | '-25C to +60C (-13F to +140F)
Realative humidity |  |  | 0% ~ 100% RH
Max. operating altitude |  | 4,000 m (13,123ft.) (Derating above 2000m)
Cooling |  |  | Smart air cooling
Display |  | LED Indicators; Integrated WLAN + FusionsSolar App
Communication | RS485; WLAN/Ethernet via Smart Dongle-WLAN-FE (Optional) 4G/3G/2G via Smart Dongle-4G (Optional)
Weight (with mounting plate) |  |  | 21 kg (46.4 lb)
Dimensions (W x H x D) (incl. mounting plate) |  | 546 mm x 460 mm x 228 mm (21.5 in x 18.1 in x 9.0 in)
Ip rating |  |  | IP65
Optimizer Compatibility
Dc MBUS compatible optimizer |  | SUN2000-450W-P2, SUN2000-600W-P, MERC-1100W-P, MERC-1300W-P
Standards Compliance
Safety |  | EN/IEC 62109-1, EN/IEC 62109-2
Grid connection standards | G99, EN 50549, CEI 0-21, CEI O-16, VDE-AR-N-4105, VDE-AR-N-4110, C10/11, ABNT, VFR 2019, UNE 217001, UNE 217002, RD 244, TOR D4, IEC61727, IEC62116