## Sheet1
MODEL | Volats-12K-H4 | Volats-14K-H4
Battery Input
Battery Type | Lead-acid or Li-Ion | Lead-acid or Li-Ion
Battery Voltage Range (V) | 40-60 | 40-60
Max. Charge Current (A) | 250 | 280
Max. Discharge Current (A) | 250 | 280
Charging Curve | 3 Stages/Equalization | 3 Stages/Equalization
External Temperature Sensor | Optional | Optional
Charging Strategy for Li-Ion Battery | Self-Adaption to BMS | Self-Adaption to BMS
PV String Input
Max. DC Input Power (W) | 18,000 | 20,000
PV Input Voltage (V) | 650 (160-800) | 650 (160-800)
MPPT Range (V) | 200-700 | 200-700
Full Load DC Voltage Range (V) | 260-680 | 260-680
Start-Up Voltage (V) | 150 | 150
PV Input Current (A) | 26+17 | 34+20
Max. PV Isc (A) | 26+17 | 34+20
No. of MPPT Trackers | 2 | 2
No. of Strings per MPPT Trackers | 2+1 | 2+1
AC Output
Rated AC Output and UPS Power (W) | 12,000 | 14,000
Max. AC Output Power (W) | 13200 | 15400
Peak Power (off-grid) | 2 times of rated power, 10s | 1.8 times of rated power, 10s
AC Output Rated Current (A) | 18.2/17.4 | 21.1/20.3
Max. AC Current (A) | 27.3/26.1 | 27.6/26.4
Max. Continuous AC Passthrough (A) | 50 | 50
Power Factor | 0.8 leading to 0.8 lagging | 0.8 leading to 0.8 lagging
Output Frequency and Voltage (V) | 50/60Hz, 380/400Vac (Triple phase) | 50/60Hz, 380/400Vac (Triple phase)
Grid Type | Three phase | Three phase
Current Harmonic Distortion | THD≤3% (Linear load ≤1.5%) | THD≤3% (Linear load ≤1.5%)
Efficiency
Max. Efficiency | 97.9% | 97.9%
Euro Efficiency | 96% | 96%
MPPT Efficiency | 99.9% | 99.9%
Protection
Integrated Protections | Integrated | Integrated
PV Arc Fault Detection | Optional | Optional
Output Over Voltage Protection | DC Type II/AC Type III | DC Type II/AC Type III
Certifications and Standards
Grid Regulation | CEI-0-21, VDE-AR-N 4105, NRS 097, IEC 61727, G99, G98, VDE 0126-1-1, RD 1699, C10-11
Safety Regulation | IEC/EN62109-1, IEC/EN62109-2
EMC | IEC/EN61000-6-1,IEC/EN 61000-6-2, IEC/EN 61000-6-3, IEC/EN 61000-6-4
General Data
Operating Temperature Range (°C) | -45~60, ±5 Derating | -45~60, ±5 Derating
Cooling | Smart Cooling | Smart Cooling
Noise (dB) | ≤45 | ≤45
Communication with BMS | CAN, RS485 | CAN, RS485
Weight (kg) | 44 | 45
Dimensions (mm) | 510×630×290 | 510×630×290
Protection Degree | IP65 | IP65
Installation Style | Wall-mounted | Wall-mounted
Warranty | 5 Years