## Sheet1
Model | SM-6K-5G3P+ | SM-8K-5G3P+ | SM-10K-5G3P+ | SM-12K-5G3P+ | SM-15K-5G3P+
Efficiency
Max. Efficiency | 98.2% | 98.2% | 98.4% | 98.4% | 98.4%
European Efficiency | 97.8% | 97.8% | 98% | 98% | 98%
MPPT Efficiency |  |  | >99%
Input(PV)
Max. Input Power (KW) | 7.8 | 10.4 | 13 | 15.6 | 19.5
Max. Input Voltage |  |  | 1000V
rated Input Voltage |  |  | 620V
Max. Input Current | 26A(2*13A) |  |  | 39A(26A+13A)
Max.short Circuit Current | 30A(2*15A) |  |  | 45A(2*15A+15A)
Start Input Voltage/Min. Operating Voltage |  |  | 200V/160V
MPPT Operating Voltage Range |  |  | 160V-960V
MPPT Operating Voltage Range (Full-Load) | 300V-900V | 380V-800V | 470V-800V | 380V-800V | 470V-800V
Max.Number of PV Strings |  | 2{1/1} |  | 3{2/1}
No. of MPPTs |  |  | 2
Output(Grid)
Rated AC Active Power | 6,000W | 8,000W | 10,000W | 12,000W | 15000W
Max. AC Apparent Power | 6,600VA | 8,800VA | 11,000VA | 13,200VA | 16,500VA
Max. AC Active Power | 6,600W | 8,800W | 11,000W | 13,200W | 16,500W
Max. AC Output Current | 3*10A | 3*13A | 3*16A | 3*18.2A | 3*22.7A
Rated AC Voltage |  |  | 380V/400V,3W+N+PE
AC Voltage Range* |  |  | 277V-520V(Adjustable)
Grid Frequency Range** |  |  | 50Hz/60Hz
THDi |  |  | 45Hz-55Hz/55Hz-65Hz(Adjustable)
DC Current Injection |  |  | <3%(Rated Power)
Power Factor |  |  | <0.5%In
Protection |  | > 0.99 Rated power(Adjustable 0.8 Leading - 0.8Lagging)
DC Switch |  |  | Support
Anti-islanding Protection |  |  | Support
AC Overcurrent Protection |  |  | Support
AC short circuit Protection |  |  | Support
DC reverse connection |  |  | Support
Surge Arrester |  |  | AC Type III
Insulation detection |  |  | Support
Leakage Current protection |  |  | Support
General
Topology |  |  | Transformerless
IP Rating |  |  | IP65
Night Self Consumption |  |  | < 1W
Cooling |  |  | Natural Cooling
Operating Temperature Range |  |  | -25º-60º
Relative Humidity range |  |  | 0-100%
Max. Operating Altitude |  |  | 4000m
noise |  |  | <30dB
Dimensions (W*H*D) |  |  | 400*500*190mm
Weight | 18.9KG |  |  |  | 21.8KG
HMI & COM
Display |  | Bluetooth, APP, LED & LCD
Communication |  | WiFi, RS485, GPRS(Optional)
Certification
Safety |  | IEC62109-1, IEC62109-2
Others |  | IEC 60068, IEC 61683
Grid Code |  | VDE-AR-N 4105, IEC61727, IEC62116, EN 50549, IEEE 1547, AS 4777
Warranty |  |  | 6 Years/10 Years(Optional)