## Sheet1
Type | Suntrio Plus 25K | Suntrio Plus 33K | Suntrio Plus 40K | Suntrio Plus 50K | Suntrio Plus 60K
Input (DC)
Max. DC Power [W] | 30300 | 36300 | 48400 | 60500 | 72000
Max. DC Voltage [V] |  |  | 1000
MPPT Voltage Range[V] |  | 180 - 900 |  | 280 - 900
Nominal DC Voltage[V] |  |  | 600
Start Voltage[V] |  | 200 |  | 300
Min. DC Voltage[V] |  | 180 |  | 250
Max .DC Input Current PV1 / PV2 [A] | 22/22/22 |  | 40/30/30 |  | 40/40/40
Number of MPPT |  |  | 3
Number of DC Connection Sets per MPPT | 2/2/2 |  | 4/3/3 |  | 4/4/4
DC Switch |  |  | Integrated
Output (AC)
Rated AC Power [W] (@ 230V,50Hz) | 25000 | 30000 | 40000 | 50000 | 60000
Max. AC Power [W] | 27500 | 33000 | 44000 | 55000 | 60000
Rated AC Current[A] | 37.9 | 45.5 | 61 | 76 | 87
Max.AC Current [A] | 42 | 50 | 65 | 80 | 90
Nominal AC voltage/ range |  | 3/N/PE,220/280V, 230/400V, 240/415V, 180V-280V/312V-485V
Grid frequency / range |  | 50Hz, 60Hz / 44Hz-55Hz, 54-65Hz
Power factor, adjustable [cos Fay) |  | 0.8 leading ~ 0.8 lagging
Toltal Harmonic Distortion (THDi) |  | < 3 % ( at nominal power )
Feed-in |  | 3L + N + PE
Efficiency
Max. Efficiency | 98.6% | 98.8% | 98.8% | 98.8% | 98.9%
Euro Efficiency (@ 600Vdc) | 98.4% | 98.5% | 98.5% | 98.5% | 98.6%
MPPT Accuracy |  |  | > 99.5%
Protection
Internal Over-voltage Protection |  |  | Integrated
DC Insulation Monitoring |  |  | Integrated
DCI Monitoring |  |  | Integrated
GFCI Moniting |  |  | Integrated
Grid Monitoring |  |  | Integrated
AC Short Circuit Current Protection |  |  | Integrated
LVRT |  |  | Integrated
Thermal Protection |  |  | Integrated
AC Surge Protection |  |  | Integrated (II)
String Current Monitoring |  |  | Integrated
Anti-PID Module |  |  | Optional
DC Surge Protection |  |  | Integrated (II)
DC Fuse |  |  | Optional
Anti-island protection monitoring |  |  | AFD
Interface
DC Connection |  |  | MC4/H4
AC Connection |  |  | Terminal Block
LCD & LED Display |  | 3.5 inch Graphic LCD Display
Display Language |  |  | English
Communication port |  |  | 2*RS485 1*RS232
Communication |  |  | Wi-Fi/GPRS/Ethernet ( Optional )
General Data
Topology |  |  | Transformerless
Consumption at Night[W] |  |  | <0.6
Consumption at Standby [W] |  |  | <10
Operating Temperature Range |  |  | 25C to +60C ( 45C to 60C with derating )
Cooling Method |  |  | Intelligent fan
Ambient Humidity |  |  | 0% to 100% Non-condensing
Altitude |  |  | 3000m ( >2000m power derating )
Noise [dBA] |  |  | < 35
Ingress Protection |  |  | IP65 ( Indoor & Outdoor Installation )
Mounting |  |  | Rear Panel
Dimensions (H*W*D)[mm] | 700*530*260 |  |  | 800*550*280
Weight [kg] | 48 |  |  | 68
Standard Warranty [Year] |  | 5 ( Standard ) / 10 / 15 / 20 / 25 ( Optional )
Certificates | IEC62109-1/2, IEC61000-6-2/3, IEC61683, IEC60068-2,IEC62116,IEC61727,PEA/MEA,NRS 097-2-1,UTE-C-15-712-1,VDEO126-1-1/A1, VDE-AR-N 4105, AS4777.2,AS4777.2,AS4777.3,C-TICK,CQC NB/T 32004,G83-2,G59-3,NBR 16149,NBR 16150,TF 3.2.1