## Sheet1
Type | Suntrio Plus 30K | Suntrio Plus 33K | Suntrio Plus 40K | Suntrio Plus 50K | Suntrio Plus 60K
Input DC
Max. PV Array Power [Wp]@STC | 40000 | 40000 | 60000 | 65000 | 78000
Max. DC Voltage [V] | 1000 | 1000 | 1000 | 1000 | 1000
MPPT Voltage Range [V] | 180-900 | 180-900 | 280-900 | 280-900 | 280-900
Nominal DC Voltage [V] | 600 | 600 | 600 | 600 | 600
Start Voltage [V] | 200 | 200 | 300 | 300 | 300
Min. DC Voltage [V] | 180 | 180 | 250 | 250 | 250
Max. DC Input Current PV1 / PV2 [A] | 22/22/22 | 22/22/22 | 44/33/33 | 44/44/44 | 44/44/44
Number of MPPT | 3 | 3 | 3 | 3 | 3
Number of DC Connection Sets per MPPT | 2/2/2 | 2/2/2 | 4/3/3 | 4/4/4 | 4/4/4
DC Switch | Integrated | Integrated | Integrated | Integrated | Integrated
Output AC
Rated AC Power [W] (@230V,50Hz) | 30000 | 30000 | 40000 | 50000 | 60000
Max. AC Power [VA] | 30000 | 33000 | 44000 | 55000 | 60000
Rated AC Current [A] | 43.5 | 45.5 | 58 | 72.5 | 87
Max. AC Current [A] | 50 | 50 | 65 | 80 | 90
Nominal AC voltage/ range | 3/N/PE, 220/380V,230/400V,240/415V;180V-280V/312V-485V
Grid frequency/ range |  | 50Hz,60Hz/44Hz-55Hz,54Hz-65Hz
Power factor, adjustable |  |  | 0.8 leading-0.8 lagging
Total Harmonic Distortion (THDi) |  | < 3% (at nominal power) | < 3% (at nominal power)
Feed-in Grid |  |  | 3L+N+PE
Efficiency
Max. Efficiency | 98.8% | 98.8% | 98.8% | 98.8% | 98.9%
Euro Efficiency (at 600Vdc) | 98.5% | 98.5% | 98.5% | 98.5% | 98.6%
MPPT Accuracy |  |  | >99.5%
Protection
Internal Over-voltage Protection |  |  | Integrated
DC Insulation Monitoring |  |  | Integrated
GFCI Monitoring |  |  | Integrated
Grid Monitoring |  |  | Integrated
AC Short Circuit Current Protection |  |  | Integrated
Thermal Protection |  |  | Integrated
AC Surage Protection |  |  | Ⅱ(Integrated)
Low Voltage Ride Through |  |  | Integrated
String Current Monitoring |  |  | Integrated
Anti-PID Module |  |  | Optional
DC fuse |  |  | Optional
DC Surge Protection |  |  | Ⅱ(Integrated)
Anti-island protection monitoring |  |  | AFD
Interface
DC Connection |  |  | MC4/H4
AC Connection |  |  | Terminal Block
LCD Display |  |  | 3.5 inch Graphic LCD Display
Display Language |  |  | English
Communication Port |  |  | 2*RS485+1*RS232
Communication Mode |  |  | Wi-Fi/GPRS/Ethernet (Optional)
General Data
Topology |  |  | Transformerless
Consumption at Night [W] |  |  | <0.6
Consumption at Standby [W] |  |  | <10
Operating Temperature Range |  |  | -25°C to +60°C(45°C to 60°C with derating)
Cooling Method |  |  | Intelligent Fan
Ambient Humidity |  |  | 0 to 100% Non-condensing
Altitude |  |  | 3000m (>2000m power derating)
Noise dB |  |  | <35
Ingress Protection |  |  | IP65 (Indoor & Outdoor Installation)
Mounting |  |  | Rear Panal
Dimensions (H*W*D) [mm] |  | 700*530*260 |  | 800*550*282
Net Weight (Kg) |  | 48 |  | 68
Standard Warranty [Year] |  |  | 5 (standard)/10/15/20/25 (Optional)
Certificates | IEC/EN62109-1/2, EN61000-6-2/3, IEC61683, IEC60068-2, IEC62116, IEC61727, VDE0126-1-1/A1, VDE-AR-N 4105, CQC NB/T 32004, G99,NBR 16149, NBR 16150,C10/11,EN50438, RD1669,UNE206006,UNE206007,G59/3