## Sheet1
Technical Data | Sunny Tripower 15000TL | Sunny Tripower 20000TL | Sunny Tripower 25000TL
Input (DC)
Max. generator power | 27000 Wp | 36000 Wp | 45000 Wp
DC rated power | 15330 W | 20440 W | 25550 W
Max. input voltage | 1000V | 1000 V | 1000 V
MPP voltage range / rated input voltage | 240 V to 800 V / 600 V | 320 V to 800 V / 600 V 390 V to 800 V / 600 V
Min. input voltage / start input voltage | 150 V / 188 V | 150 V / 188 V 150 V / 188 V
Max. input current input A / input B | 33 A / 33 A | 33 A / 33 A | 33 A / 33 A
Number of independent MPP inputs / strings per MPP input | 2 / A:3; B:3 | 2 / A:3; B:3 | 2 / A:3; B:3
Output (AC)
Rated power (at 230 V, 50 Hz) | 15000 W | 20000 W 25000 W
Max. AC apparent power | 15000 VA | 20000 VA 25000 VA
AC nominal voltage | 3 / N / PE; 220 V / 380 V 3 / N / PE; 230 V / 400 V 3 / N / PE; 240 V / 415 V | 3 / N / PE; 220 V / 380 V 3 / N / PE; 230 V / 400 V 3 / N / PE; 240 V / 415 V
AC voltage range | 180 V to 280 V | 180 V to 280 V
AC grid frequency / range | 50 Hz / 44 Hz to 55 Hz 60 Hz / 54 Hz to 65 Hz | 50 Hz / 44 Hz to 55 Hz 60 Hz / 54 Hz to 65 Hz
Rated power frequency / rated grid voltage | 50 Hz / 230 V | 50 Hz / 230 V
Max. output current / rated output current | 29 A / 21.7 A | 29 A / 29 A 36.2 A / 36.2 A
Power factor at rated power / Adjustable displacement power factor | 1 / 0 overexcited to 0 underexcited | 1 / 0 overexcited to 0 underexcited
THD | ≤ 3% | ≤ 3%
Feed-in phases / connection phases | 3/3 | '3/3
Efficiency
Max. efficiency / European Efficiency | 98.4% / 98.0% | 98.4% / 98.0% 98.3% / 98.1%
Protective devices
DC-side disconnection device | ● | ●
Ground fault monitoring / grid monitoring | ● / ● | ● / ●
DC surge arrester (Type II) can be integrated | ○ | ○
DC reverse polarity protection / AC short-circuit current capability / galvanically isolated | ● / ● / — | ● / ● / —
All-pole sensitive residual-current monitoring unit | ● | ●
Protection class (according to IEC 62109-1) / overvoltage category (according to IEC 62109-1) | I / AC: III; DC: II | I / AC: III; DC: II
General data
Dimensions (W / H / D) | 661 / 682 / 264 mm (26.0 / 26.9 / 10.4 inch) | 661 / 682 / 264 mm (26.0 / 26.9 / 10.4 inch)
Weight | 61 kg (134.48 lb) | 61 kg (134.48 lb)
Operating temperature range | −25 °C to +60 °C (−13 °F to +140 °F | −25 °C to +60 °C (−13 °F to +140 °F
Noise emission (typical) | 51 dB(A) | 51 dB(A
Self-consumption (at night) | 1 W | 1 W
Topology / cooling concept | Transformerless / Opticool | Transformerless / Opticool
Degree of protection (as per IEC 60529) | IP65 | IP65
Climatic category (according to IEC 60721-3-4) | 4K4H | 4K4H
Maximum permissible value for relative humidity (non-condensing) | 100% | 100%
Features / function / Accessories
DC connection / AC connection | SUNCLIX / spring-cage termina | SUNCLIX / spring-cage terminal
Display | ○ | ○
Interface: RS485, Speedwire / Webconnect | ○ / ● | ○ / ●
Data interface: SMA Modbus / SunSpec Modbus | ● / ● | ● / ●
Multifunction relay / Power Control Module | ○ / ○ | ○ / ○
OptiTrac Global Peak / Integrated Plant Control / Q on Demand 24/7 | ● / ● / ● | ● / ● / ●
Off-Grid capable / SMA Fuel Save Controller compatible | ● / ● | ● / ●
Guarantee: 5 / 10 / 15 / 20 years | ● / ○ / ○ / ○ | ● / ○ / ○ / ○
Planned certificates and permits * Does not apply to all national appendices of EN 50438 | ANRE 30, AS 4777, BDEW 2008, C10/11:2012, CE, CEI 0-16, CEI 0-21, DEWA 2.0, EN 50438:2013*, G59/3, IEC 60068-2-x, IEC 61727, IEC 62109-1/2, IEC 62116, MEA 2013, NBR 16149, NEN EN 50438, NRS 097-2-1, PEA 2013, PPC, RD 1699/413, RD 661/2007, Res. n°7:2013, SI4777, TOR D4, TR 3.2.2, UTE C15-712-1, VDE 0126-1-1, VDE-AR-N 4105, VFR 2014 |  | ANRE 30, AS 4777, BDEW 2008, C10/11:2012, CE, CEI 0-16, CEI 0-21, DEWA 2.0, EN 50438:2013*, G59/3, IEC 60068-2-x, IEC 61727, IEC 62109-1/2, IEC 62116, MEA 2013, NBR 16149, NEN EN 50438, NRS 097-2-1, PEA 2013, PPC, RD 1699/413, RD 661/2007, Res. n°7:2013, SI4777, TOR D4, TR 3.2.2, UTE C15-712-1, VDE 0126-1-1, VDE-AR-N 4105, VFR 2014
Type designation | STP 15000TL-30 | STP 20000TL-30 | STP 20000TL-30