## Sheet1
Technical Data | Sunny Tripower 5000TL | Sunny Tripower 6000TL | Sunny Tripower 7000TL | Sunny Tripower 8000TL | Sunny Tripower 9000TL | Sunny Tripower 10000TL | Sunny Tripower 12000TL
Input (DC)
Max. generation power | 9000 | 9000Wp | 13500 Wp 13500 Wp 13500 Wp |  |  | 13500 Wp 18000 Wp
Max. input voltage | 1000V | 1000V | 1000 V 1000 V 1000 V |  |  | 1000 V | 1000 V
MPP voltage range / rated input voltage | 245 V to 800 V / 580 V | 295 V to 800 V / 580V | 290 V to 800 V / 580 V 330 V to 800 V / 580 V 370 V to 800 V / 580 V |  |  | 370 V to 800 V / 580 V 440 V to 800 V / 580 V
Min. input voltage / start input voltage | 150 V / 188 V | 150 V / 188 V | 150 V / 188 V 150 V / 188 V 150 V / 188 V |  |  | 150 V / 188 V | 150 V / 188 V
Max. input current input A / input B | 11 A / 10A | 11 A / 10 A | 15 A / 10 A 15 A / 10 A 15 A / 10 A |  |  | 18 A / 10 A | 18 A / 10 A
Max. short-circuit current input A / input B | 17 A / 15 A | 17 A / 15 A | 25 A / 15 A 25 A / 15 A 25 A / 15 A |  |  | 25 A / 15 A | 25 A / 15 A
Number of independent MPP input / strrings per MPP input | 2 / A:2;B:2 | 2 / A:2,B:2 | 2 / A:2; B:2 2 / A:2; B:2 2 / A:2; B:2 |  |  | 2 / A:2; B:2 | 2 / A:2; B:2
Output (AC)
Rated power (at 230 V, 50 Hz) | 5000W | 6000W | 7000 W 8000 W 9000 W |  |  | 10000 W 12000 W
Max. AC apparent power | 5000 VA | 6000VA | 7000 VA 8000 VA 9000 VA |  |  | 10000 VA 12000 VA
Nominal AC voltage | 3 / N / PE; 220 / 380 V,3 / N /PE,230 / 400 V,3 / N / PE; 240 / 415 V | 3 / N / PE; 220 / 380 V, 3 / N /PE,230 / 400 V,3 / N / PE; 240 / 415 V | 3 / N / PE; 220 / 380 V 3 / N / PE; 230 / 400 V 3 / N / PE; 240 / 415 V | 3 / N / PE; 220 / 380 V 3 / N / PE; 230 / 400 V 3 / N / PE; 240 / 415 V | 3 / N / PE; 220 / 380 V 3 / N / PE; 230 / 400 V 3 / N / PE; 240 / 415 V | 3 / N / PE; 220 / 380 V 3 / N / PE; 230 / 400 V 3 / N / PE; 240 / 415 V | 3 / N / PE; 220 / 380 V 3 / N / PE; 230 / 400 V 3 / N / PE; 240 / 415 V
Nominal AC voltage range | 160 to 280 V | 160 to 280 V | 160 V to 280 V 160 V to 280 V 160 V … 280 V |  |  | 160 to 280 V | 160 to 280 V
AC grid frequency / range | 50 Hz,60Hz / -5 Hz to +5 Hz | 50 Hz,60Hz / -5 Hz to +5 Hz | 50 Hz, 60 Hz / -5 Hz to +5 Hz 50 Hz, 60 Hz / -5 Hz to +5 Hz 50 Hz, 60 Hz / -5 Hz … +5 H |  |  | 50 Hz, 60 Hz / -5 Hz to +5 Hz 50 Hz, | 50 Hz, 60 Hz / -5 Hz to +5 Hz 50 Hz,
Rated power frequency / rated grid voltage | 50 Hz / 230 V | 50 Hz / 230 V | 50 Hz / 230 V | 50 Hz / 230 V | 50 Hz / 230 V | 50 Hz / 230 V | 50 Hz / 230 V
Max. output current | 7.3 A | 7.3 A | 10.2 A 11.6 A 13.1 A |  |  | 14.5 A 17.4 A
Power factor at rated power | 1 | 1 | 1 | 1 | 1 | 1 | 1
Adjustable displacement power factor | 0.8 overexcited to 0.8 underexcited | 0.8 overexcited to 0.8 underexcited | 0.8 overexcited to 0.8 underexcited | 0.8 overexcited to 0.8 underexcited | 0.8 overexcited to 0.8 underexcited | 0.8 overexcited to 0.8 underexcited | 0.8 overexcited to 0.8 underexcited
Feed-in phases / connection phases | 3 /3 | '3 /3 | 3 / 3 | '3 / 3 | 3 / 3 | '3 / 3 | '3 / 3
Efficiency
Max. efficiency / European efficiency | 98 % / 97.1 % | 98 % / 97.4 % | 98 % / 97.5 % 98 % / 97.6 % 98 % / 97.6 % |  |  | 98 % / 97.6 % 98.3 % / 97.9 %
Protective devices
DC disconnect device | ● | ● | ● | ● | ● | ● | ●
Ground fault monitoring / grid monitoring | ● / ● | ● / ● | ● / ● | ● / ● | ● / ● | ● / ● | ● / ●
DC reverse polarity protection / AC short-circuit current capability / galvanically isolated | ● / ● / — | ● / ● / — | ● / ● / — | ● / ● / — | ● / ● / — | ● / ● / — | ● / ● / —
All-pole sensitive residual-current monitoring unit | ● | ● | ● | ● | ● | ● | ●
Protection class (according to IEC 62103)/ overvoltage category (according to IEC 60664-1) | I / III | I / III | I / III | I / III | I / III | I / III | I / III
General data
Dimensions (W / H / D) | 470 / 730 / 240mm(18.5 / 28.7 / 9.5 inch) | 470 / 730 / 240mm(18.5 / 28.7 / 9.5 inch) | 470 / 730 / 240 mm (18.5 / 28.7 / 9.5 inch) | 470 / 730 / 240 mm (18.5 / 28.7 / 9.5 inch) | 470 / 730 / 240 mm (18.5 / 28.7 / 9.5 inch) | 470 / 730 / 240 mm (18.5 / 28.7 / 9.5 inch) | 470 / 730 / 240 mm (18.5 / 28.7 / 9.5 inch)
Weight | 37 kg (81.6 Lb) | 37 kg (81.6 Lb) | 37 kg (81.6 lb) | 37 kg (81.6 lb) | 37 kg (81.6 lb) | 37 kg (81.6 lb) 38 kg / 84 lbs
Operating temperature range | -25 C to +60 C(-13F to +140F) | '-25 C to +60 C(-13F to +140F) | -25 °C to +60 °C (-13 °F to +140 °F) | -25 °C to +60 °C (-13 °F to +140 °F) | -25 °C to +60 °C (-13 °F to +140 °F) | -25°C to +60 °C (-13 °F to +140 °F | -25°C to +60 °C (-13 °F to +140 °F
Noise emission (typical) | 40 dB(A) | 40 dB(A) | 40 dB(A) | 40 dB(A) | 40 dB(A) | 40 dB(A) | 40 dB(A)
Self-consumption | 1 W | 1 W | 1 W | 1 W | 1 W | 1 W | 1 W
Topology / cooling concept | Transformerless / Opticool | Transformerless / Optional | Transformerless / Optional | Transformerless / Optional | Transformerless / Optional | Transformerless / Optional | Transformerless / Optional
Degree of protection (according to IEC 60529) | IP65 | IP65 | IP65 | IP65 | IP65 | IP65 | IP65
Climatic category (according to IEC 60721-3-4) | 4K4H | 4K4H | 4K4H | 4K4H | 4K4H | 4K4H | 4K4H
Maximum permissible value for relative humidity (non-condensing) | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Features
DC connection / AC connection | SUNCLIX / spring-cage terminal | SUNCLIX / spring-cage terminal | SUNCLIX / spring-cage terminal | SUNCLIX / spring-cage terminal | SUNCLIX / spring-cage terminal | SUNCLIX / spring-cage terminal | SUNCLIX / spring-cage terminal
Display | Graphic | Graphic | Graphic | Graphic | Graphic | Graphic | Graphic
Interface: RS485, Modbus, Speedwire / Webconnect | ○ / ● / ● | ○ / ● / ● | ○ / ● / ● | ○ / ● / ● | ○ / ● / ● | ○ / ● / ● | ○ / ● / ●
Multifunction relay / Power Control Module | ● / ○ | ● / ○ | ● / ○ | ● / ○ | ● / ○ | ● / ○ | ● / ○
Guarantee: 5 / 10 / 15 / 20 years | ● / ○ / ○ / ○ | ● / ○ / ○ / ○ | ● / ○ / ○ / ○ | ● / ○ / ○ / ○ | ● / ○ / ○ / ○ | ● / ○ / ○ / ○ | ● / ○ / ○ / ○
Certificates and permits (more available on request) | AS4777.2:2015,CE, CEI 0-21:2016, C10/11:2012,DIN EN 62109-1,EN 50438', G59/3,G83/2,IEC 61727/MEA,IEC 62109-2,NEN EN 50438,NRS 097-2-1,PPC,PPDS,RD 661/2007, RD 1699:2011,SI 4777,UTE C15-712-1,VDEO126-1-1,VDE0126-1-1,VDE AR-N4105,VFR 2013,VFR2014
Type designation | STP 5000TL-20 | SPT 5000TL-20 | SPT 5000TL-20 | SPT 5000TL-20 | SPT 5000TL-20 | SPT 5000TL-20 | SPT 5000TL-20