## Sheet1
Datasheet | SOFAR 110KTLX-G4 | SOFAR 125KTLX-G4
Input (DC)
Max. input voltage | 1100V
Rated input voltage | 625V
Start-up voltage | 200V
MPPT operating voltage range | 180-1000V
Number of MPP trackers | 10
Number of DC inputs | 20
Max. input current per MPPT | 10*40A
Max. input short circuit current | 10*50A
Output (AC)
Rated output power | 100KW
Max. apparent power | 110kVA@45°C / 100kVA@50°C | 125kVA@45°C / 110kVA@50°C
Max. output current | 167.2A@380V / 159.5A@400V / 153.1A@415V | 190A@380V / 181.2A@400V / 174A@415V
Rated grid voltage | 3/N/PE, 380V / 400V / 415V
Grid voltage range | 310 ~ 480V
Rated frequency | 50/60Hz
Grid frequency range | 45-55Hz/55-65Hz
Active power adjustable range | 0-100%
THDi | <1%(@100%P)
Power factor | 1 (adjustable +/-0.8)
Efficiency
Max. efficiency | 98.6%
European efficiency | 98.3%
Protection
DC reverse polarity protection | Yes
Anti-islanding protection | Yes
Leakage current protection | Yes
Ground fault monitoring | Yes
PV-array string fault monitoring | Yes
DC switch | Yes
AFCI | Yes
SPD | PV: type II stand, AC: type II standard
General Data
Ambient temperature range | -30°C ~ +60°C
Self-consumption at night | <1W
Topology | Transformerless
Degree of protection | IP66
Allowable relative humidity range | 0~100%
Max. operating altitude | 4000m(>3000m derating)
Weight | 75Kg
Cooling | Smart forced air cooling
Dimension (W*H*D) | 970*695*325mm
Display | LCD & Bluetooth + APP
Communication | RS485/WiFi