## Sheet1
Datasheet | SOFAR 20000TL-G2 | SOFAR 25000TL-G2 | SOFAR 30000TL-G2 | SOFAR 33000TL-G2
Input (DC)
Recommended Max. PV input power | 26600wp | 33250Wp | 39900Wp | 43890Wp
Max DC power for single MPPT | 13000W | 16000W | 18000W | 20000W
Number of MPP trackers |  | 2
Number of DC inputs | 2 for each MPPT | 3 for each MPPT | 3 for each MPPT | 3 for each MPPT
Max. input voltage |  | 1100V
Start-up voltage |  | 250V
Rated input voltage |  | 620V
MPPT operating voltage range |  | 230V-960V
Full power MPPT voltage range | 480V-850V | 460V-850V | 520V-850V | 580V-850V
Max. input current per string | 24A/24A | 28A/28A | 30A/30A | 30A/30A
Maximum DC input short circuit current per MPPT | 30A | 35A | 37.5A | 37.5A
Output (AC)
Rated power | 20000W | 25000W | 30000W | 33000W
Max. AC power | 22000VA | 27500VA | 33000VA | 36300VA
Max. Output Current | 32A | 40A | 48A | 53A
Nominal Grid voltage |  | 3/N/PE, 220/380Vac, 230/400Vac, 240/415Vac
Grid Voltage range |  | 310Vac-480Vac (According to local standard)
Nominal frequency |  | 50/60Hz
Grid Frequency Range |  | 45Hz-55Hz/54Hz-66Hz (According to local standard)
Active power adjustable range |  | 0 ~ 100%
THDi |  | <3%
Power factor |  | >0.99 (Adjustable+/-0.8)
Performance
Max efficiency | 98.2% | 98.4% | 98.4% | 98.6%
European weighted efficiency | 98% | 98.2% | 98.2% | 98.2%
Self-consumption at night |  | < 1W
MPPT efficiency |  | >99.9%
Protection
DC reversepolarity protection |  |  | Yes
DC switch |  |  | Yes
Protection class / overvoltage category |  |  | I/III
Safety protection |  | Anti islanding, RCMU, Ground fault monitoring
ARPC |  | Anti reverse power controller (optional)
Communication
Power management unit |  | According to certification and request
Standard communication mode |  | RS485, Wifi/Ethernet/GPRS(optional),SD card
Operation data storage |  | 25 years
General Data
Ambient temperature range |  | -25C ~ +60C
Topology |  | Transformer-less
Degree of protection |  | IP65
Allowable relative humidity range |  | 0 ~ 100%
Max. operating altitude |  | 2000m
Noise | <30dB | <45dB | <45dB | <45dB
Weight |  | 37Kg
Cooling | Natural | Fan | Fan | Fan
Dimension |  | 666*512*254mm
Display |  | LCD display
Warranty |  | 5 years/7 years/ 10 years
Standard
EMC |  | EN 61000-6-2, EN 61000-6-3, EN 61000-3-1 I, EN 61000-3-12
Safety standards | IEC62109-1/2,1EC62116,1EC61727,1EC-61683,1EC60068(1,2,14,30),1EC60255
Grid standards | AS/NZS 4417, VDE V 0124-100. V 0126-1-1, VDE-AR-N 4105, CEI 0-21/CEI 0-16, EN 50549, G59, P.O. 12.3, RD 1699, UTE C 15-712-1, EN 50530, NB/T32004