## Sheet1
Datasheet | SAFAR 20000TL-G2 | SOFAR 25000TL-G2 | SOFAR 30000TL-G2 | SOFAR 33000TL-G2
Input(DC)
Max. Input Power | 26000W | 32500W | 39000W | 42900W
Max Dc power for single MPPT | 13000W | 16000W | 18000W | 20000W
Number of independent MPPT |  |  | 2
Number of DC inputs | 2 for each MPPT |  | 3 for each MPPT
Max. input voltage |  | 1100V
Start-up input voltage |  | 250V
Rated input voltage | 620V | 620V | 620V | 620V
MPPT voltage range |  | 230V 960V
Full load DC voltage range | 480V 850V | 460V 850V | 520V 850V | 580V 850V
Max. input MPPT current | 24A/24A | 28A/28A | 30A/30A | 30A/30A
Output(AC)
Rated power(@230V,50Hz) | 20000W | 25000W | 30000W | 33000W
Max. AC power | 22000VA | 27500VA | 33000VA | 36300VA
Max. output current | 32A | 40A | 48A | 53A
Nominal Grid Voltage |  | 3/N/PE, 230/400Vac
Grid Voltage range |  | 310Vac-480Vac
Nominal Frequency |  | 50/60Hz
Grid Frequency range | 45~55Hz/55~65Hz(According to local standard)
Active power adjustable range |  | 0~100%
THDi |  | <3%
Power factor |  | 1(Adjustable+/0.8)
Performance
Max efficiency | 98.2% | 98.4% | 98.4% | 98.6%
European weighted efficiency | 98% | 98.2% | 98.2% | 98.2%
Self-consumption at night |  | <1W
Feed-in start power |  | 45W
MPPT efficiency |  | >99.9%
Protection
DC reverse polarity protection |  | Yes
DC switch |  | Yes
Protection class/ overvoltage |  | I/III
Safety protection |  | Anti islanding, RCMU, Ground Fault monitoring
Certification | IEC 62116, IEC 61727, IEC 61683, IEC 60068(1,2,14,30), IEC62109-1/2CE,CGCZVRT,AS4777,AS3100
ARPC |  | Anti Reverse Power Controller (Optional)
Communication
Power management unit |  | According to certification and request
Stand Communicaton Mode | RS485, Wifi (Optional), GPRS(Optional), SD card, Multi-function relay
Operating Data Storage |  | 25 Years
General data
Ambient temperature range |  | -25C…+60C
Topology |  | Transformerless
Degree of protection |  | IP65
Allowable relative humidity range |  | 0…100% no condensing
Max.operating altitude |  | <2000M
Noise | <30dB | <45dB | <45dB | <45dB
Weight |  | 37Kg
Cooling | Natural | Fan | Fan | Fan
Dimension |  | 666*512*254mm
Display |  | LCD display
Warranty |  | 5 years/7 years/10 years