## Sheet1
Datasheet | SOFAR 30000TL | SOFAR 33000TL | SOFAR 36000TL | SOFAR 40000TL
Input (DC)
Recommended Max. PV input power | 39900Wp | 43890Wp | 47880Wp | 53200Wp
Max DC power for single MPPT | 15360W | 17000W | 20400 | 20400W
Number of MPP trackers |  |  | 2
Number of DC inputs |  |  | 4 for each MPPT
Max. input voltage |  |  | 10000V
Start-up voltage |  |  | 350V
Rated input voltage | 600V | 600V | 600V | 700V
MPPT operating voltage range |  |  | 250V-960V
Full power MPPT voltage range | 480V-800V | 480-800V | 500V-800V | 560V-800V
Max. input MPPT current | 332A/32A | 35A/35A | 38A/38A | 35A/35A
Max. input current per string |  |  | 12A
Maximum DC input short circuit current per MPPT | 40A | 40A | 42A | 40A
Output (AC)
Rated power | 30000W | 33000W | 36000W | 40000W
Max. AC power | 30000VA | 33000W | 36000W | 40000W
Max. Output Current | 43A | 48A | 54A | 48A
Nominal Grid voltage | 3/N/PE, 220/380Vac, 230/400vac, 240/415Vac |  | 3/N/PE or 3/PE, 277/480Vac
Grid Voltage range | 310Vac-480Vac (According to local standard) |  | 422Vac-528Vac (According to local standard)
Nominal frequency |  | 50/60Hz
Grid Frequency Range |  | 45Hz-55Hz/54Hz-66Hz (According to local standard)
Active power adjustable range |  | 0~100%
THDi |  | <3%
Power factor |  | >0.99 (adjustable +/-0.8)
Performance
Max efficiency | 98.5% | 98.5% | 98.5% | 98.7%
European weighted efficiency | 98.2% | 98.2% | 98.2% | 98.4%
Self-consumption at night |  | <1W
MPPT efficiency |  | >99.9%
Protection
DC reversepolarity protection |  | Yes
DC switch |  | Yes
Protection class / overvoltage category |  | I/III
Safety protection |  | Anti islanding, RCMU, Ground fault monitoring
ARPC |  | Anti reverse power controller (optional)
Input/output SPD (II) |  | Optional
Communication
Power management unit |  | According to certification and request
Standard communication mode | RS485, Wifi/Ethernet/GPRS (Optional), SD card, Multi-function relay
Operation data storage |  | 25Years
General Data
Ambient temperature range |  | '-25C ~+60C
Topology |  | Transformer-less
Degree of protection |  | IP65
Allowable relative humidity range |  | 0~100%
Max. operating altitude |  | 2000m
Noise | <30dB | <45dB | <45dB | <45dB
Weight |  | 50Kg
Cooling | Natural | Fan | Fan | Fan
Dimension |  | 777*564*298mm
Display |  | LCD display
Warranty |  | 5 years/7 years / 10 years
Standard
EMC |  | EN 6 1000-6-2, EN 6 1000-6-4
Safety standards | IEC62109-1/2, IEC62116, IEC61727, IEC-61683, IEC60068 (1,2,14,30)
Grid standards | AS/NZS 4777, AS/NZS 61000, VDE V 0124-100, V0126-I-I, VDE-AR-N 4105, CEI 0-21/CEI 0-16, EN50549, G59, RD1699,UTE CI 5-712-I, EN50530