## Sheet1
Datasheet | SOFAR 50000TL | SOFAR 60000TL | SOFAR 70000TL-HV
Input (DC)
Recommended Max. PV input power | 66500Wp | 79800Wp | 93100Wp
Max DC power for single MPPT | 22000W,16000W,16000W | 22000W,22000W,22000W | 26000W,26000W,26000W
Number of MPP trackers |  | 3
Number of DC inputs | 4/3/3 | 4/4/4 | 4/4/4
Max. input voltage |  | 1000V
Start-up voltage |  | 350V
Rated input voltage |  | 600V
MPPT operating voltage range |  | 250V-950V
Full power MPPT voltage range | 530V-800V | 530V-800V | 660V-800V
Max. input MPPT current | 40A/30A/30A | 40A/40A/40A | 40A/40A/40A
Max. input current per string |  | 12A
Maximum DC input short circuit current per MPPT | 48A/36A/36A | 48A | 48A
Output (AC)
Rated power | 50000W | 60000W | 70000W
Max. AC power | 50000VA | 60000VA | 75000VA
Max. Output Current | 80A | 90A | 90A
Nominal Grid voltage | 3/N/PE, 220/380Vac, 230/400Vac, 240/415Vac |  | 3/N/PE or 3/PE,277/480Vac
Grid Voltage range | 310Vac-480Vac (According to local standard) |  | 422Vac-528Vac
Nominal frequency |  | 50/60Hz
Grid Frequency Range |  | 45Hz-55Hz/54Hz-66Hz (According to local standard)
Active power adjustable range |  | 0 ~ 100%
THDi |  | <3%
Power factor |  | >0.99(Adjustable+/-0.8)
Performance
Max efficiency | 98.5% | 98.6% | 98.6%
European weighted efficiency | 98.3% | 98.4% | 98.4%
Self-consumption at night |  | <1W
MPPT efficiency |  | >99.9%
Protection
DC reversepolarity protection |  | Yes
DC switch |  | Yes
Protection class / overvoltage category |  | I/III
Safety protection |  | PV: type II standard, AC: type II optional
ARPC |  | Anti islanding, RCMU, Ground fault monitoring
Input/output SPD (II) |  | Anti reverse power controller (optional)
Communication
Power management unit |  | According to Certification and request
Standard communication mode | RS485, Wifi/Ethernet/GPRS(optional), SD card, Multi-function relay
Operation data storage |  | 25 years
General Data
Ambient temperature range |  | -25C ~ +60C
Topology |  | Transformer-less
Degree of protection |  | IP65
Allowable relative humidity range |  | 0 ~ 100%
Max. operating altitude |  | 4000m
Noise |  | <=60dB
Weight | 68Kg | 70Kg | 70Kg
Cooling |  | Fan
Dimension |  | 713*737*297mm
Display |  | LCD display
Warranty |  | 5 years/7 Years/ 10 years
Standard
EMC | EN 61000-6-2,EN 61000-6-4, EN 61000-3-II, EN 61000-3-12
Safety standards | IEC62109-I/2, IEC62116, IEC61727, IEC-61683, IEC60068(1,2,14,30)
Grid standards | AS/NZS 4777, VDC V 0124-100, V 0124-100, VO126-1-1, VDE-AR-N 4105, BDEW, CEI 0-21/CEI 0-16, UNE 206 007-I, EN50549, G59, EN50530, NB/T32004