## Sheet1
Datasheet | GTX 3000-H4 | GTX 3000-H5 | GTX 3000-H6 | GTX 3000-H7 | GTX 3000-H8 | GTX 3000-H9 | GTX 3000-H10
Parameters
Battery Module Quantity | 4 | 5 | 6 | 7 | 8 | 9 | 10
Nominal Voltage | 204.8V | 256V | 307.2V | 358.4V | 409.6V | 460.8V | 512V
Max. Charge Voltage | 230.4V | 288V | 345.6V | 403.2V | 460.8V | 518.4V | 576V
Min. Discharging Voltage | 182.4V | 228V | 273.6V | 319.2V | 364.8V | 410.4V | 456V
Nominal Energy | 10kWh | 12.5kWh | 15kWh | 17.5kWh | 20kWh | 22.5kWh | 25kWh
Available Energy(90%DOD) | 9kWh | 11.25kwh | 13.5kWh | 15.75kWh | 18kWh | 20.25kWh | 22.5kWh
Dimension(mm) | 515*480*770 | 515*480*895 | 515*480*1020 | 515*480*1145 | 515*480*1270 | 515*480*1395 | 515*480*1520
Weight | 138k | 168kg | 198kg | 228kg | 258kg | 288kg | 318kg
Protection Class |  |  |  | IP65
Cooling |  |  |  | Natural
Nominal Charging Current |  |  |  | 25A
Max. Continuous Charging Current |  |  |  | 30A
Nominal Discharge Current |  |  |  | 25A
Max. Continuous Discharge Current |  |  |  | 30A
Working Temperature |  |  |  | -20C ~ 60C
Storage Temperature |  |  |  | <=25C, 12 months,<=35C, 6 months, <=45C, 3 months
Environmental humidity |  |  | <=95% RH (No condensation)
Operating Altitude |  |  | <=2000m
Scale |  |  | Suggest no more than 4 parallel
Certification |  |  | UN38.3, IEC62619, IEC62040-1,SAA etc
Cycle Life |  |  | 6000@80%DOD / 25C / 0.5C / 60%EOL
Battery module parameters
Battery type |  |  |  | LifePO4, Lithium Iron Phosphate
Nominal Voltage |  |  |  | 51.2V
Nominal Capacity |  |  |  | 50AH
Weight |  |  |  | 30kg
Dimension |  |  |  | 515*478.8*125mm
Protection |  |  |  | IP65