## Sheet1
MODEL | X3-FTH-75K | X3-FTH-80K | X3-FTH-100K | X3-FTH-110K | X3-FTH-120K | X3-FTH-125K | X3-FTH-136K-MV | X3-FTH-150K-MV
DC INPUT
Max. PV array input power [kWp] | 120 | 120 | 150 | 165 | 180 | 188 | 204 | 225
Max. PV input voltage [V] |  |  | 1100
Nominal input voltage [V]* | 580/600 | 580/600 | 580/600 | 580/600 | 580/600 | 580/600 | 730/785 | 730/785
Startup voltage [V] |  |  | 200
MPP tracker voltage range [V] |  |  | 180-1000
No. of MPP trackers | 9 | 9 | 9 | 9 | 12 | 12 | 12 | 12
Strings per MPP tracker |  |  | 2
Max. PV input current per MPPT [A] |  |  | 32
Isc PV Array Short Circuit current per MPPT [A] |  |  | 46
AC OUTPUT
Rated AC output power [kW] | 75 | 80 | 100 | 110 | 120 | 125 | 136 | 150
Rated AC output current [A]* | 113.7/108.7 | 121.3/116 | 151.6/145 | 166.7/159.5 | 181.9/174 | 189.4/181.2 | 157.1/145.4 | 173.2/160.4
Max. AC output apparent power [kVA] | 75 | 80 | 100 | 110 | 120 | 125 | 136 | 150
Max. AC output current [A]* | 113.7/108.7 | 133.4/127.6 | 166.7/159.5 | 183.4/175.4 | 200/191.3 | 200/191.3 | 172.8/160 | 190.6/176.5
Nominal AC voltage [V] |  | 220/380, 230/400, 3/N/PE, 3/PE |  |  |  | 500/540,3P3W+PE
AC voltage range [V]** |  | 304 ~ 480 |  |  | 425 ~ 594
Nominal AC frequency/AC frequency range [Hz]** |  |  | 50/60; ±5
THDi (Rated power) [%] |  |  | <3
Power Factor range |  |  | 0.8 leading ~ 0.8 lagging
SYSTEM DATA
MPPT efficiency [%] |  |  | 99.9
Max. efficiency[%] | 98.6 | 98.6 | 98.6 | 98.6 | 98.6 | 98.6 | 99 | 99
Ingress protection |  |  | IP66
Operating ambient temperature range [°C] |  |  | -30~+60 (Derating above 45)
Max. operation altitude [m] |  |  | 4000 (Derating above 3000)
Relative humidity [%] |  |  | 0~100
Dimensions [W×H×D] [mm] |  |  | 985x660x327.5
Weight [kg] | 83 | 83 | 83 | 83 | 87 | 87 | 87 | 87
Cooling concept |  |  | Smart fan cooling
Communication interfaces |  | RS485 / USB / DRM / PLC(Optional)
Optional monitoring dongle |  |  | Pocket WiFi/LAN/4G
Display |  |  | LCD(16x2, optional)/LEDx4
PROTECTION
Over/under voltage protection |  |  | YES
DC isolation protection |  |  | YES
Grid monitoring |  |  | YES
DC injection monitoring |  |  | YES
Residual current detection |  |  | YES
Anti-islanding protection |  |  | YES
String fault detection |  |  | YES
SPD (DC/AC) |  |  | Type II / Type II
Arc-fault circuit interrupter(AFCI) |  |  | Optional
AC terminals over temperature detection |  |  | YES
AC auxiliary power supply(APS) |  |  | Optional
Power line communication(PLC) |  |  | Optional
STANDARD
Safety |  |  | IEC/EN 62109-1; IEC/EN 62109-2; NB/T 32004
EMC |  |  | IEC/EN 61000; NB/T 32004
Certification |  | EN 50549; AS4777.2; VDE4105; IEC 61727; IEC 62116; IEC 61683; IEC 60068; EN 50530; NB/T 32004