## Sheet1
MODEL | X3-PRO-8K-G2 | X3-PRO-10K-G2 | X3-PRO-12K-G2 | X3-PRO-15K-G2 | X3-PRO-17K-G2 | X3-PRO-20K-G2 | X3-PRO-25K-G2 | X3-PRO-30K-G2
DC INPUT
Max. PV array input power [Wp] | 12000 | 15000 | 18000 | 22500 | 25500 | 30000 | 37500 | 45000
Max. PV input voltage [V] | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100
Start start up voltage[V] | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Nominal Input Voltage[V] | 65 | 650 | 650 | 650 | 650 | 650 | 650 | 650
MPP tracker voltage range [V] |  |  |  | 160~980
No. of MPP trackers | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3
Strings per MPP tracker | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Max. PV input current [A] | 32/32 | 32/32 | 32/32 | 32/32 | 32/32 | 32/32 | 32/32 | 32/32
Isc PV Array Short Circuit current [A] | 40/40 | 40/40 | 40/40 | 40/40 | 40/40 | 40/40 | 40/40 | 40/40
AC OUTPUT
Rated AC output power [kW] | 8000 | 10000 | 12000 | 15000 | 17000 | 20000 | 25000 | 30000
Rated AC output current [A]* | 12.2/11.6 | 15.2/14.5 | 18.2/17.4 | 22.8/21.8 | 25.8/24.7 | 30.3/29 | 37.9/36.3 | 45.5/43.5
Max. AC output apparent power [VA] | 8800 | 11000 | 13200 | 16500 | 18700 | 22000 | 27500 | 30000
Max. AC output current [A] | 13.2 | 16 | 19.3 | 24.2 | 27.5 | 33.6 | 41.8 | 45.5
Nominal AC voltage/AC voltage range [V]** |  |  | 220/380V, 230/400V, 3/N/PE, 3/PE; 95-285V
Nominal AC frequency/AC frequency range [Hz]** |  |  | 50/60, +-5
Power Factor range |  |  | 0.8 leading ~ 0.8 lagging
THDi (Rated power) [%] |  |  | <3
SYSTEM DATA
Max. e ciency [%] | 98.2 | 98.2 | 98.2 | 98.3 | 98.3 | 98.3 | 98.5 | 98.5
Euro e ciency [%] | 97.7 | 97.7 | 97.7 | 97.8 | 97.8 | 97.8 | 98 | 98
Standby consumption (Night) [W] |  |  |  | <3
Ingress protection |  |  |  | IP66
Operating ambient temperature range [°C] |  |  |  | -30~+60
Max. operation altitude [m] |  |  |  | 4000
Relative humidity [%] |  |  |  | 0~100
Typical noise emission [dB] | <35 | <35 | <35 | <55 | <55 | <55 | <55 | <58
Storage temperature [°C] |  |  |  | -30~+60
Dimensions (W×H×D) [mm] |  |  |  | 482x417x186
Weight [kg] |  | 24.5 |  | 26 |  | 28
Cooling concept |  | Natural cooling |  |  |  | Smart fan cooling
Communication interfaces |  |  | USB / RS485 / DRM, Optional: Meter
Optional monitoring dongle |  |  | Pocket WiFi/LAN/4G
Display |  |  | 2 x LED + LCD (16 x 2) / APP
PROTECTION
Over/under voltage protection |  |  | YES
DC isolation protection |  |  | YES
Grid monitoring |  |  | YES
DC injection monitoring |  |  | YES
Residual current detection |  |  | YES
Anti-islanding protection |  |  | YES
Over Temp protection |  |  | YES
SPD (DC/AC) |  |  | Type II / Type II
AC auxiliary power supply (APS) |  |  | Optional
Arc-fault circuit interrupter (AFCI) |  |  | Optional
STANDARD
Safety |  | IEC/EN 62109-1；IEC/EN 62109-2；NB/T 32004
EMC | EN IEC 61000-6-1/2/3/4，EN IEC 61000-3-2/11，EN 61000-3-3/12，EN 55011，EN 62920IEC/EN 61000；NB/T 32004
Certification | VDE4105, EN 50549, AS 4777.2, IEC 61727, IEC 62116, IEC 61683, IEC 60068, EN 50530, NB/T 32004