## Sheet1
Models | 100K | 110K
INPUT DC
Max. input voltage | 1100 V
Rated voltage | 600 V
Start-up voltage | 195 V
MPPT voltage range | 180-1000 V
Max. input current | 10*26A
Max. short circuit current | 10* 40 A
MPPT number/Max. input strings number | '10/20
OUTPUT AC
Rated output power | 100KW | 110KW
Max. apparent output power | 110KVA | 121 KVA
Max. output power | 110 KW | 121KW
Rated grid voltage | 2/N/PE,220V / 280V, 230 V / 400 V
Rated grid frequency | 50 Hz / 60 Hz
Rated grid output current | 152.0A / 144.3 A | 167.1A / 158.8 A
Max. output current | 167.1A / 158.8 A | 183.8 A / 174.7 A
Power factor | >0.99 (0.8 leading - 0.8 lagging)
THDi | <3%
EFFICIENCY
Max. efficiency | 98.7%
EU efficiency | 98.3%
PROTECTION
DC reverse-polarity protection | Yes
Short circuit protection | Yes
Output over current protection | Yes
Surge protection | DC Type II / AC Type II (AC Type I optional)
Grid monitoring | Yes
Anti-islanding protection | Yes
Temperature protection | Yes
Strings monitoring | Yes
I/V Curve Scanning | Yes
Integrated PID recovery | Optional
Integrated AFCI (DC arc-fault circuit protection) | Yes
Integrated DC switch | Yes
Integrated AC switch | Optional
GENERAL DATA
Dimensions (W*H*D) | 1065*567*344.5mm
Weight | 91 kg
Topology | Transformerless
Self-consumption (night) | <2 W
Operating ambient temperature range | '-30 ~ +60C
Relative humidity | 0 - 100%
Ingress protection | IP66
Cooling concept | Intelligent redundant fan-cooling
Max. operating altitude | 4000m
Grid connection standard | VDE-AR-N 4105, VDE V 0124, VDE V 0126-1-1, UTE C15-712-1, NRS 097-1-2, G98,G99, EN 50549-1/-2, RD 1699,TOR,UNE 206006, UNE 206007-1, CEI0-21, IEC61727, DEWA
Safety/EMC standard | IEC/EN 62109-1/-2,IEC/EN 61000-6-2/-4
FEATURES
DC connection | MC4 connection
AC connection | OT terminal (max. 185mm^2)
Display | LCD
Communication | RS485, Optional:Wi-Fi, GPRS,PLC