## Sheet1
Model Name | Solis-3P5k-4G
Input DC
Max. DC input power(kW) | 24
Max. DC input voltage(V) | 1000
Start-up voltage(V) | 180
MPPT Voltage range (V) | 160-850
Max. input current(A/B) | 22A+22A
Max. Short Circuit current for each MPPT | 34.3A+34.3A
MPPT number/Max input string number | 2/A:2;B:2
Output AC
Rated output power(KW) | 20
Max.apparent output power(KVA) | 22
Max. output power(KW) | 22
Rated grid voltage(V) | 400
Rated grid frequency (Hz) | 50/60
Grid frequency range(Hz) | 47-52 or 57-62
Operation Phase | Three Phase
Rated grid output current (A) | 28.9
Max. output current(A) | 31.8
Power Factor (at rated output power) | 0.8leading … 0.8lagging
THDi (at rated power) | <1.5 %
DC injection current | <0.5%In
Efficiency
Max. efficiency | 98.7%
EU efficiency | 97.1%
MPPT efficiency | >99.5%
Protection
DC reverse-polarity protection | Yes
Short circuit protection | Yes
Output over current protection | Yes
Output over voltage protection | Yes
Insulation resistance monitoring | Yes
Residual current detection | Yes
Surge protection | Yes
Grid monitoring | Yes
Islanding protection | Yes
Temperature protection | Yes
Integrated DC switch | Optional
General Data
Dimensins(mm) | 310W*563H*219D
Weight (kg) | 17.3
Topology | Transformerless
Self consumption (night) | <1W (Night)
Operating ambient temperature range | -25~60C
Relative humidity | 0~100%
Ingress protection | IP65
Noise emission (typical) | <30 dBA
Cooling concept | Natural convection
Max. operation altitude | 4000m
Designed Lifetime | >20 Years
Grid connection standard | EN50438, AS4777, VDEO126-1-1,IEC61727,G98
Safty/EMC standard | IEC62109-1/-2,AS3100,EN61000-6-1,EN61000
Features
DC connection | MC4
AC connection | Terminal connectors
Display | LCD, 2 x 20 Z
Communication connections | 4 pins RS485 connector
Monitoring | WiFi or GPRS
Warranty | 5 years (extand to 20 years)

## Sheet2
Solis 3P 4G Three Phase Range
160V-850V MPPT voltage range-ultra low startup
Dual MPPT design with precise MPPT algorithm
THDi<1.5%, low harmonic distortion against grid
Over 98.3% Max. effciency
Multiple protection Levels
RS485, WIFi/LAN/GPRS (optional) interface
WiFi monitoring available-Android and Apple App store available
5 years standard warranty, 20 years optional upgrade