## Sheet1
Model Name | Solis-80K-5G | Solis-100K-HV-5G | Solis-110K-BHV-5G
Input DC
Max.input voltage |  | 1100V
Rated voltage |  | 600V
Start-up voltage |  | 195V
MPPT voltage range |  | 180-1000V
Max.input current | 9*26A |  | 10*26A
Max.short circuit current | 9*40A |  | 10*40A
MPPT number/Max.input strings number | 9/18 |  | 10/20
Output AC
Rated output power | 80KW | 100KW | 110KW
Max.apparent output power | 88KVA | 110KVA | 121KVA
Max.output power | 88KW | 110KW | 121KW
Rated grid voltage | 3/N/PE,220/380V,230/400V | 3/PE/, 480V | 3/PE,540V
Rated grid frequency |  | 50/60Hz
Rated grid output current | 121.6A | 120.3A | 117.6A
Max.output current | 133.7A | 132.3A | 129.4A
Power Factor |  | >0.99(0.8leading - 0.8lagging)
THDi |  | <3%
Efficiency
Max.efficiency | 98.7% |  | 99%
EU efficiency | 98.3% |  | 98.5%
Protection
DC reverse-polarity protection |  | Yes
Short circuit protection |  | Yes
Output over current protection |  | Yes
Surge protection |  | DC Type II / AC Type II(AC Type I optional)
Grid monitoring |  | Yes
Anti-islanding protection |  | Yes
Strings monitoring |  | Yes
I/V Curve scanning |  | Yes
Anti-PID function |  | Optional
Integrated AFCI(dc arc-fault circuit protection) |  | Optional
Integrated DC switch |  | Yes
Integrated AC switch |  | Optional
General Data
Dimensions (W*H*D) |  | 1050*567*314.5mm(with AC switch)
Weight |  | 82Kg
Topllogy |  | Transformerless
Self consumption |  | <2W(night)
Operating ambient temperature range |  | -25 ~ +60C
Relative humidity |  | 0-100%
Ingress protection |  | IP66
Cooling concept |  | Intelligent redundant fan-cooling
Max.operating altitude |  | 400m
Grid connection standard |  | VED-AR--N4105,VDE V 0124,VED V0126-1-1,UTE C15-712-1,NRS097-1-2,G98,G99,EN50549-1/-2,RD 1699,UNE 206006, UNE 206007-1, IEC 61727,DEWA
Safety/EM standard |  | IED 62109-1/-2,IEC 62116,EN 61000-6-2/-4
Features
DC connection |  | MC4 connector
AC connection |  | OT terminal (max. 185mm^2)
Display |  | LCD, 2 x 20Z
Communication |  | RS485,Option:WiFi,GPRS,PLc

## Sheet2
Over 99% Max.effciency.
Wide voltage range and low startup voltage.
9/10 MPPT design with precise MPPT algorithm.
THDI<3%, low harmonic distortion against grid.
Anti-resonance, supporting over 6MW parallelled in one transformer.
Perfect commercial site monitoring solution.
Intelligent redundant fan-cooling.
Strings intelligent monitoring,Smart I-V curve Diagnosis supported.
Fuse free design to avoid fire hazard.
Type II surge arrester for both DC and Ac , type I surge arrestor optional.
Leakage current repression technology
Volt-watt work mode integrated
DC input reverse alarm
Optional anti-PID function integrated
Integrated DC switches, AC switch optional