## Sheet1
Model Name | Solis-80K-5G | Solis-100K-HV-5G | Solis-110K-BHV-5G
Input DC
Max. Input voltage |  | 1100V
Rated voltage |  | 600V
Start-up voltage |  | 195V
Mppt voltage range |  | 180-1000V
Max. input current | 9*26A |  | 10*26A
Max. short circuit current | 9*40A |  | 10*40A
MPPT number/Max, input strings number | 9/18 |  | 10/20
Output AC
Rated output power | 80KW | 100KW | 110KW
Max. apparent output power | 88KVA | 110KVA | 121KVA
Max. output power | 88KW | 110KW | 121KW
Rated grid voltage | 3/N/PE, 220/380V,230/400V | 3/PE, 480V | 3/PE, 540V
Rated grid frequency |  | 50/60Hz
Rated grid output current |  | 120.3A
Max. output current |  | 132.3A
Power Factor |  | >0.99(o.8 leading - 0.8 lagging)
THDi |  | <3%
Efficiency
Max. efficiency | 98.7% |  | 99%
EU efficiency | 98.3% |  | 98.5%
Protection
DC reverse-polarity protection |  | Yes
Short circuit protection |  | Yes
Output over current protection |  | Yes
Surge protection |  | DC Type II / AC Type II (AC Type I optional)
Grid monitoring |  | Yes
Anti-islanding protection |  | Yes
Strings monitoring |  | Yes
I/V Curve scanning |  | Yes
Anti-PID function |  | Optional
Integrated AFCI(DC arc-fault circuit protection) |  | Optional
Integrated DC switch |  | Yes
Integrated AC switch |  | Optional
General Data
Dimensions (W*H*D) |  | 1050*567*314.5 mm (with AC switch)
Weight |  | 82Kg
Topolkogy |  | Transformerless
Self consumption |  | <2W (night)
Operating ambient temperature range |  | -25 ~ +60C
Relative humidity |  | 0-100%
Ingress protection |  | IP66
Cooling concept |  | Intelligent redundant fan-cooling
Max. operation altitude |  | 4000m
Grid connection standard |  | VDE-AR-N 4105,VDE V 0124 ,VDE V 0126-1-1, UTE c15-712-1, NRS 097-1-2, G98, G99,EN 50549-1/-2, RD 1699,UNE 206007-1, IEC 61727, DEWA
Safety/EMC standard | IEC 62109-1/-2, IEC 62116, EN 61000-6-2/-4
Features
DC Connection |  | MC4 connector
AC Connection |  | OT terminal (max. 185mm^2)
Display |  | LCD, 2 x 20 Z
Communication |  | RS485, Optional:WiFi, GPRS, PLC

## Sheet2
Over 99% Max. effciency
Wide voltage range and low startup voltage
9/10 MPPT design with precise MPPT algorithm
THDi<3%, Low harmonic distortion against grid
Anti- resonance, supporting over 6MW parallelled in one transformer
Perfect commercial site monitoring solution
Intelligent redundant fan-cooling
Strings intelligent monitoring, Smart I-V Curve Diagnosis supported
Fuse free design to avoid fire hazard
Type II surge arrester for both DC and AC, Type I surge arrestor optional
Leakage current repression technology
Volt-watt work mode integrated
DC input reverse alarm
Optional anti-PID function integrated
Integrated Dc switches, AC switch optional